## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle, Hapur.
Name of Work: FOR SHIFTING OF 33KV LINE, 11KV LINE, L.T. LINE AND OTHER ASSOCIATED WORKS, IN THE WAY OF GANGA EXPRESSWAY, IN DEPOSIT SCHEME, IN THE JURISDICTION OF EDD-GARHMUKTESHWER, UNDER EDC., HAPUR.
Tender No: 23(W)/EDCH/2024-25
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | FOR SHIFTING OF 33KV LINE AND OTHER ASSOCIATED WORKS, IN THE WAY OF GANGA EXPRESSWAY, IN DEPOSIT SCHEME, IN THE JURISDICTION OF EDD-GARHMUKTESHWER, UNDER EDC., HAPUR. (All work will be completed as per Sanctioned estimate). | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Carriage of all petty material of estimate, from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. | BI01010001010000000000000515BI0100001113 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Carriage of all type cable/conductor of estimate from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 3001 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | Carriage of ST Pole 11 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road,as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 20 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.04 | Erection of double pole structure with all accessories on ST Pole 11 mtr. long, fabrication and fixing of M.S. Top & Dropper Channel, M.S. T/F Angle, E-Bracket, 33 KV Pin insulator with Pin, Disc Insulator with Disc fitting etc., as per RESPO Drawing/Norms by providing all clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts, and jumpering etc work, and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | Erection of Tri-pole structure with all accessories on ST Pole 11 mtr. long, fabrication and fixing of M.S. Top & Dropper Channel, M.S. T/F Angle, E-Bracket, 33 KV Pin insulator with Pin, Disc Insulator with Disc fitting etc., as per RESPO Drawing/Norms by providing all clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts, and jumpering etc work, and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.06 | Erection & Fixing of ST Pole 11 mtr. long in 33 KV line after digging of suitable pits including fixing of requisite accessories as per RESPO Drawing/Norms by providing F-Bracket made of M.S. Flat of size 50x6 mm, holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 15 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.07 | Laying, Stringing and final sagging of ACSR Dog Conductor, as per RESPO/Drawing Norms and as per direction of site incharge | BI01010001010000000000000515BI0100001115 | 3001 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.08 | Grouting & fixing of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:4:8 cement, sand, 40mm brick ballast as per drg. Including back filling, proper ramming etc and fixing tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing as per RESPO Drawing/Norms by providing all grouting material and stay clamp made of M.S. Flat of size 50x6mm with proper size bolts & nuts & loops, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 16 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.09 | Earthing of supports with MS earth Rod of (20x2540)mm long including excavation of pit and driving M.S. Rod 3.0 M apart from support and 0.5m below the ground level and connection below the earth electrodes with the help of G.I. wire & earthing lugs as per RESPO Drawing/Norms by providing proper size nuts & bolts, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 20 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.1 | Grouting of ST supports in CC 1:4:8 (Cement, sand & 40mm brick ballast) Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, up to ground level, 300mm plinth above the ground level with CC 1:3:6 (Cement, core sand and Stone grit) with mufting as per drawing, work includes back filling & proper ramming by providing all required grouting materials, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 20 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | Wrapping of barbed wire on 33KV ST poles as anti-climbing device for a length of 0.9mtrs. Wire pitch/gap 13mm and fixing upper and lower end keeping lower end at a hieght of 2.75 mtr from the ground complete, including providing & fixing of lower end & upper end clamps made of M.S. Flat 40X5mm complete with nuts & bolts and all other required material and T&P., as per RESPO/Drawing Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 20 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | Painting of following supports, including Channel, X-Arm, Clamps etc. with 02 coats of synthetic enamel paint/aluminum paint, with one coat of primer red oxide paint including cost of all required material, labour and T&P., as per RESPO/Drawing Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 20 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | Providing & Fixing of Danger Board, including fixing of all accessories by providing all required materials (like suitable clamps, nuts & bolts etc.) as per RESPO/Drawing Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 20 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | Providing & Fixing of Number Plate alongwith all required accessories (like suitable clamps, nuts & bolts etc.) as per RESPO/Drawing Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 20 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | Dismantling of existing 33KV Line and old & used conductor and opening of all accessories. (Iron/steel Scrap 30Kg., Conductor-60Kg, including carriage of above material form site of work to JE Store/ESC-Hapur, with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 0.9 | Qtl. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | Dismantling of old & used STP and opening of all accessories, including carriage of above material form site of work to JE Store/ESC-Hapur, with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 6 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.17 | Jumpering and line energisation work properly as per RESPO/Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 2 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2 | FOR SHIFTING OF 11KV LINE AND OTHER ASSOCIATED WORKS, IN THE WAY OF GANGA EXPRESSWAY, IN DEPOSIT SCHEME, IN THE JURISDICTION OF EDD-GARHMUKTESHWER, UNDER EDC., HAPUR. (All work will be completed as per Sanctioned estimate). | BI01010001010000000000000515BI0100001115
2.01 | Carriage of all petty material of estimate, from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.02 | Carriage of all type cable/conductor of estimate from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 4135 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.03 | Carriage of ST Pole 11 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road,as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 25 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.04 | Erection of double pole structure with all accessories on ST Pole 11 mtr. long, fabrication and fixing of M.S. Top & Dropper Channel, M.S. T/F Angle, E-Bracket, 11 KV Pin insulator with Pin, Disc Insulator with Disc fitting etc., as per RESPO Drawing/Norms by providing all clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts, and jumpering etc work, and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 5 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.05 | Erection & Fixing of ST Pole 11 mtr. long in 11 KV line after digging of suitable pits including fixing of requisite accessories as per RESPO Drawing/Norms by providing F-Bracket made of M.S. Flat of size 50x6 mm, holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 15 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.06 | Trenchless laying (270X2=540mtrs. Double Circuit) of 140/160mm O/D PN-4PE-80 PN-4 grade UV stabilized HDPE pipe as per IS of 6meter, for laying of underground Cable as per RESPO/Norms, including cost of above HDPE pipe, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 540 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.07 | Laying of LT XLPE Cable 3.5x240Sqmm, undergound (160x2=320 Double Circuit) into HDPE Pipe, spare cable shall be left in the loop shape at both ends as per RESPO/Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 400 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.08 | Laying of 11KV XLPE Cable 3x185Sqmm, undergound (110x2=220 Double Circuit) into HDPE Pipe, spare cable shall be left in the loop shape at both ends as per RESPO/Norms and as per direction of site incharge | BI01010001010000000000000515BI0100001115 | 300 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.09 | Providing & Fixing of G.I. pipe 6"dia Class-B over 11 KV 3X185 Sq.mm XLPE cable and LT XLPE Cable before mounting the cable at double pole. The work includes fitting of clamps, sealing of top and bottom of pipe and one end of pipe is to be burried under earth about 500mm earch including mounting and clamping the cable on double pole structure and making connection with overhead line at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 24 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.1 | Making and filling of 11KV Cable Jointing Kit 3x185Sqmm, after duly plumbing and taping of suitable XLPE Cable, providing, fixing and crimping of proper size good quality lugs, including cost of lugs and tape etc., as per RESPO Norms, and as per direction of site incharge. |  | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.11 | Laying, Stringing and final sagging of ACSR Weasel Conductor, as per RESPO/Drawing Norms and as per direction of site incharge |  | 2195 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.12 | Grouting & fixing of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:4:8 cement, sand, 40mm brick ballast as per drg. Including back filling, proper ramming etc and fixing tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing as per RESPO Drawing/Norms by providing all grouting material and stay clamp made of M.S. Flat of size 50x6mm with proper size bolts & nuts & loops, as per direction of site incharge. |  | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.13 | Earthing of supports with MS earth Rod of (20x2540)mm long including excavation of pit and driving M.S. Rod 3.0 M apart from support and 0.5m below the ground level and connection below the earth electrodes with the help of G.I. wire & earthing lugs as per RESPO Drawing/Norms by providing proper size nuts & bolts, as per direction of site incharge. |  | 24 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.14 | Grouting of ST supports in CC 1:4:8 (Cement, sand & 40mm brick ballast) Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, up to ground level, 300mm plinth above the ground level with CC 1:3:6 (Cement, core sand and Stone grit) with mufting as per drawing, work includes back filling & proper ramming by providing all required grouting materials, as per direction of site incharge. |  | 25 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.15 | Wrapping of barbed wire on 11KV ST poles as anti-climbing device for a length of 0.9mtrs. Wire pitch/gap 13mm and fixing upper and lower end keeping lower end at a hieght of 2.75 mtr from the ground complete, including providing & fixing of lower end & upper end clamps made of M.S. Flat 40X5mm complete with nuts & bolts and all other required material and T&P., as per RESPO/Drawing Norms and as per direction of site incharge. |  | 25 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.16 | Painting of following supports, including Channel, X-Arm, Clamps etc. with 02 coats of synthetic enamel paint/aluminum paint, with one coat of primer red oxide paint including cost of all required material, labour and T&P., as per RESPO/Drawing Norms and as per direction of site incharge. |  | 25 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.17 | Providing & Fixing of Danger Board, including fixing of all accessories by providing all required materials (like suitable clamps, nuts & bolts etc.) as per RESPO/Drawing Norms and as per direction of site incharge. |  | 25 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.18 | Providing & Fixing of Number Plate alongwith all required accessories (like suitable clamps, nuts & bolts etc.) as per RESPO/Drawing Norms and as per direction of site incharge. |  | 25 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.19 | Erection & Fixing of 11KV. TPMO set on ST Pole 11mtr long, by providing all fixing required as per RESPO/Drawing Norms and as per direction of site incharge. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.2 | Erection & Fixing of 11KV. Fuse set on ST Pole 11mtr long,by providing all fixing required as per RESPO/Drawing Norms and as per direction of site incharge |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.21 | Safely removal of 63KVA transfomers on existing Double Pole and safely carriage to new site of work with loading and unloading at both ends, as per RESPO/Drawing Norms and as per direction of site incharge. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.22 | Mounting, Placing of old 63KVA Transformers and connecting from LT/HT side connection and completion work properly,as per RESPO/Drawing Norms and as per direction of site incharge. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.23 | Dismantling of existing 11KV Line and old & used conductor and opening of all accessories. (Iron/steel Scrap 60Kg., Conductor-120Kg, 11KV XLPE cable 3x185sqmm-300mtrs.-300Kg.) including carriage of above material form site of work to JE Store/ESC-Hapur, with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. |  | 4.8 | Qtl. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.24 | Dismantling of old & used PCC/STP and opening of all accessories, including carriage of above material form site of work to JE Store/ESC-Hapur, with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. |  | 19 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.25 | Providing and fixing of PG Clamps as per RESPO/Drawing Norms and as per direction of site incharge. |  | 12 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.26 | Jumpering and line energisation work properly as per RESPO/Norms and as per direction of site incharge. |  | 4 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3 | FOR SHIFTING OF L.T. LINE AND OTHER ASSOCIATED WORKS, IN THE WAY OF GANGA EXPRESSWAY, IN DEPOSIT SCHEME, IN THE JURISDICTION OF EDD-GARHMUKTESHWER, UNDER EDC., HAPUR. (All work will be completed as per Sanctioned estimate).
3.01 | Carriage of all petty material of estimate, from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.02 | Carriage of all type cable/conductor of estimate from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading at both ends, as per direction of site incharge. |  | 500 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.03 | Carriage of ST Pole 11 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road,as per direction of site incharge. |  | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.04 | Trenchless laying (210X2=420mtrs. Double Circuit) of 140/160mm O/D PN-4PE-80 PN-4 grade UV stabilized HDPE pipe as per IS of 6meter, for laying of underground Cable as per RESPO/Norms, including cost of above HDPE pipe, as per direction of site incharge. |  | 420 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.05 | Laying of LT XLPE Cable 3.5x240Sqmm, undergound (210x2=420 Double Circuit) into HDPE Pipe, spare cable shall be left in the loop shape at both ends as per RESPO/Norms and as per direction of site incharge. |  | 500 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.06 | Providing & Fixing of G.I. pipe 6"dia Class-B over LT XLPE cable and LT XLPE Cable before mounting the cable at double pole. The work includes fitting of clamps, sealing of top and bottom of pipe and one end of pipe is to be burried under earth about 500mm earch including mounting and clamping the cable on double pole structure and making connection with overhead line at both ends, as per direction of site incharge. |  | 12 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.07 | Grouting & fixing of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:4:8 cement, sand, 40mm brick ballast as per drg. Including back filling, proper ramming etc and fixing tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing as per RESPO Drawing/Norms by providing all grouting material and stay clamp made of M.S. Flat of size 50x6mm with proper size bolts & nuts & loops, as per direction of site incharge. |  | 5 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.08 | Earthing of supports with MS earth Rod of (20x2540)mm long including excavation of pit and driving M.S. Rod 3.0 M apart from support and 0.5m below the ground level and connection below the earth electrodes with the help of G.I. wire & earthing lugs as per RESPO Drawing/Norms by providing proper size nuts & bolts, as per direction of site incharge. |  | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.09 | Grouting of ST supports in CC 1:4:8 (Cement, sand & 40mm brick ballast) Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, up to ground level, 300mm plinth above the ground level with CC 1:3:6 (Cement, core sand and Stone grit) with mufting as per drawing, work includes back filling & proper ramming by providing all required grouting materials, as per direction of site incharge. |  | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.1 | Wrapping of barbed wire on 11KV ST poles as anti-climbing device for a length of 0.9mtrs. Wire pitch/gap 13mm and fixing upper and lower end keeping lower end at a hieght of 2.75 mtr from the ground complete, including providing & fixing of lower end & upper end clamps made of M.S. Flat 40X5mm complete with nuts & bolts and all other required material and T&P., as per RESPO/Drawing Norms and as per direction of site incharge. |  | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.11 | Painting of following supports, including Channel, X-Arm, Clamps etc. with 02 coats of synthetic enamel paint/aluminum paint, with one coat of primer red oxide paint including cost of all required material, labour and T&P., as per RESPO/Drawing Norms and as per direction of site incharge. |  | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.12 | Providing & Fixing of Danger Board, including fixing of all accessories by providing all required materials (like suitable clamps, nuts & bolts etc.) as per RESPO/Drawing Norms and as per direction of site incharge. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.13 | Providing & Fixing of Number Plate alongwith all required accessories (like suitable clamps, nuts & bolts etc.) as per RESPO/Drawing Norms and as per direction of site incharge. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.14 | Dismantling of old & used 20Kgs. steel and 04Nos. STP and opening of all accessories, including carriage of above material form site of work to JE Store/ESC-Hapur, with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. |  | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.15 | Providing and fixing of PG Clamps as per RESPO/Drawing Norms and as per direction of site incharge. |  | 12 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
3.16 | Jumpering and line energisation work properly as per RESPO/Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 2 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information