## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.0 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority:- Superintending Engineer,ECDC, Ghaziabad, PVVNL.
Name of Work:- Fire Fighting System related Works at Electricity Store Centre Joya Distt.-Amroha as per recommendation of Fire safety Audit under the scheme of Business Plan 2024-25.
Contract No:- T.S. No. 15/ECDC/GZB/2024-25
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Complete design & Drawing of Fire Fighting System at Store Center By Authorised Designer as per site Requirements, direction of E/I and guidelines provided by CPWD specification of works Part-V (Wet Riser and sprinkler system 2020).( NSI ) | BI01010001010000000000000515BI0100001205 | 1 | Job | 15000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15000 | 15000 | #VALUE!
2 | Supply, Laying and testing of ISI marked Jindal, T.T Swastic, Prakash, Surya, or equivalent make of 80 MM dia MS pipe Class-C pipe of wall thickness = 4.85 mm (Heavy class) (specification as per IS 1239) for hydrant system including transportation of all materials up to worksite, loading, unloading and proper stacking at site, cutting of pipe of required length, edge preparation, welding, fixing and erection of pipes with M.S. flat iron strip & all specials i.e. elbow, bends, tees and flange, rubber gasket, nuts & bolts etc. in proper position and alignment etc. including excavation of trenches and back filling of earth, cutting of walls and floors if required and repair of the same as per direction of E/I and supports of pipe as per layout and jointing by welding, aligning the pipe line painting with a one Coat of primer coat and two coats of fire red colour paint of approved make and Quality & hydraulic testing as per direction of E/I Including cost of all Materials, Labours and T&P etc. as per direction of E/I. ( NSI ) | BI01010001010000000000000515BI0100001206 | 36 | RM | 1600 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 57600 | 57600 | #VALUE!
3 | Supply, Laying and testing of ISI marked Jindal, T.T Swastic, Prakash, Surya, or equivalent make 100 mm dia Class "C" pipe of wall thickness = 5.4 mm MS pipe (heavy class) (specification as per IS 1239) for hydrant system including transportation of all materials up to worksite, loading, unloading and proper stacking at site, cutting of pipe of required length, edge preparation, welding, fixing and erection of pipes with M.S. flat iron strip & all specials i.e. elbow, bends, tees and flange, rubber gasket, nuts & bolts etc. in proper position and alignment etc. including excavation of trenches and back filling of earth, cutting of walls and floors if required and repair of the same as per direction of E/I and supports of pipe as per layout and jointing by welding, aligning the pipe line painting with a one Coat of primer coat and two coats of fire red colour paint (P.O. red enamel paint) of approved make and Quality & hydraulic testing as per direction of E/I Including cost of all Materials, Labours and T&P etc. as per direction of E/I.NSI | BI01010001010000000000000515BI0100001207 | 35 | RM | 2135 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 74725 | 74725 | #VALUE!
4 | Supply, Laying and testing of ISI marked Jindal, T.T Swastic, Prakash, Surya, or equivalent make 150 mm dia Class "C" pipe of wall thickness = 5.4 mm MS pipe (Heavy class) (specification as per IS 1239) for hydrant system including transportation of all materials up to worksite, loading, unloading and proper stacking at site, cutting of pipe of required length, edge preparation, welding, fixing and erection of pipes with M.S. flat iron strip & all specials i.e. elbow, bends, tees and flange, rubber gasket, nuts & bolts etc. in proper position and alignment etc. including excavation of trenches and back filling of earth, cutting of walls and floors if required and repair of the same as per direction of E/I and supports of pipe as per layout and jointing by welding, aligning the pipe line painting with a one Coat of primer coat and two coats of fire red colour paint (P.O. red enamel paint) of approved make and Quality & hydraulic testing as per direction of E/I Including cost of all Materials, Labours and T&P etc. as per direction of E/I. (NSI) | BI01010001010000000000000515BI0100001208 | 320 | RM | 2673 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 855360 | 855360 | #VALUE!
5 | Supply, Laying and testing of ISI marked Jindal, T.T Swastic, Prakash, Surya, or equivalent make 200 mm dia Class "C" pipe of wall thickness MS pipe (Heavy class) (specification as per IS 1239) for hydrant system including transportation of all materials up to worksite, loading, unloading and proper stacking at site, cutting of pipe of required length, edge preparation, welding, fixing and erection of pipes with M.S. flat iron strip & all specials i.e. elbow, bends, tees and flange, rubber gasket, nuts & bolts etc. in proper position and alignment etc. including excavation of trenches and back filling of earth, cutting of walls and floors if required and repair of the same as per direction of E/I and supports of pipe as per layout and jointing by welding, aligning the pipe line painting with a one Coat of primer coat and two coats of fire red colour paint (P.O. red enamel paint) of approved make and Quality & hydraulic testing as per direction of E/I Including cost of all Materials, Labours and T&P etc. as per direction of E/I. ( NSI ) | BI01010001010000000000000515BI0100001209 | 48 | RM | 4280 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 205440 | 205440 | #VALUE!
6 | Supply, Laying and testing of ISI marked Jindal, T.T Swastic, Prakash, Surya, or equivalent make 50 mm dia Class "C" pipe of wall thickness = 4.47 mm MS pipe (heavy class) (specification as per IS 1239) for hydrant system including transportation of all materials up to worksite, loading, unloading and proper stacking at site, cutting of pipe of required length, edge preparation, welding, fixing and erection of pipes with M.S. flat iron strip & all specials i.e. elbow, bends, tees and flange, rubber gasket, nuts & bolts etc. in proper position and alignment etc. including excavation of trenches and back filling of earth, cutting of walls and floors if required and repair of the same as per direction of E/I and supports of pipe as per layout and jointing by welding, aligning the pipe line painting with a one Coat of primer coat and two coats of fire red colour paint (P.O. red enamel paint) of approved make and Quality & hydraulic testing as per direction of E/I Including cost of all Materials, Labours and T&P etc. as per direction of E/I. NSI | BI01010001010000000000000515BI0100001210 | 18 | RM | 1045 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 18810 | 18810 | #VALUE!
7 | Supply, Laying and testing of ISI marked Jindal, T.T Swastic, Prakash, Surya, or equivalent make of 25 mm dia Class "C" pipe of wall thickness = 4.05 mm MS pipe (heavy class) (specification as per IS 1239) for hydrant system including transportation of all materials up to worksite, loading, unloading and proper stacking at site, cutting of pipe of required length, edge preparation, welding, fixing and erection of pipes with M.S. flat iron strip & all specials i.e. elbow, bends, tees and flange, rubber gasket, nuts & bolts etc. in proper position and alignment etc. including excavation of trenches and back filling of earth, cutting of walls and floors if required and repair of the same as per direction of E/I and supports of pipe as per layout and jointing by welding, aligning the pipe line painting with a one Coat of primer coat and two coats of fire red colour paint (P.O. red enamel paint) of approved make and Quality & hydraulic testing as per direction of E/I Including cost of all Materials, Labours and T&P etc. as per direction of E/I. ( NSI ) | BI01010001010000000000000515BI0100001211 | 122 | RM | 625 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 76250 | 76250 | #VALUE!
8 | Providing and Fixing one coat of 4mm thick ‘PYPKOTE’ or COATEK anti rust pipe protection layer of approved make and quality including approved make primer as per manufactures specification and over lap of 25mm to make an impermeable layer on above MS Pipe 80MM dia size in trenches structural/ masonary etc. complete including surface prepration, cost of all Materials, Labours and T&P etc. as per direction of E/I. NSI | BI01010001010000000000000515BI0100001212 | 17 | RM | 293 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4981 | 4981 | #VALUE!
9 | Providing and Fixing one coat of 4mm thick ‘PYPKOTE’ or COATEK anti rust pipe protection layer of approved make and quality including approved make primer as per manufactures specification and over lap of 25mm to make an impermeable layer on above MS Pipe size 200mm dia (under ground pipe) in trenches structural/ masonary etc. complete including surface prepration, cost of all Materials, Labours and T&P etc. as per direction of E/I. ( NSI ) | BI01010001010000000000000515BI0100001213 | 10 | RM | 795 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7950 | 7950 | #VALUE!
10 | Providing and Fixing one coat of 4mm thick ‘PYPKOTE’ or COATEK anti rust pipe protection layer of approved make and quality including approved make primer as per manufactures specification and over lap of 25mm to make an impermeable layer on above MS Pipe size 150mm dia (under ground pipe) in trenches structural/ masonary etc. complete including surface prepration, cost of all Materials, Labours and T&P etc. as per direction of E/I. NSI | BI01010001010000000000000515BI0100001214 | 9 | RM | 575 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5175 | 5175 | #VALUE!
11 | Providing and Fixing one coat of 4mm thick ‘PYPKOTE’ or COATEK anti rust pipe protection layer of approved make and quality including approved make primer as per manufactures specification and over lap of 25mm to make an impermeable layer on above MS Pipe size 100mm dia (under ground pipe) in trenches structural/ masonary etc. complete including surface prepration, cost of all Materials, Labours and T&P etc. as per direction of E/I. ( NSI ) | BI01010001010000000000000515BI0100001215 | 4 | RM | 390 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1560 | 1560 | #VALUE!
12 | Providing and Fixing one coat of 4mm thick ‘PYPKOTE’ or COATEK anti rust pipe protection layer of approved make and quality including approved make primer as per manufactures specification and over lap of 25mm to make an impermeable layer on above MS Pipe size 50mm dia (under ground pipe) in trenches structural/ masonary etc. complete including surface prepration, cost of all Materials, Labours and T&P etc. as per direction of E/I. ( NSI ) | BI01010001010000000000000515BI0100001216 | 14 | RM | 200 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2800 | 2800 | #VALUE!
13 | Providing and Fixing one coat of 4mm thick ‘PYPKOTE’ or COATEK anti rust pipe protection layer of approved make and quality including approved make primer as per manufactures specification and over lap of 25mm to make an impermeable layer on above MS Pipe size 25mm dia (under ground pipe) in trenches structural/ masonary etc. complete including surface prepration, cost of all Materials, Labours and T&P etc. as per direction of E/I. ( NSI ) | BI01010001010000000000000515BI0100001217 | 17 | RM | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1700 | 1700 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | Supply, fixing and testing in position ISI marked and approved make cast iron butter fly valve including all interal fittings of 80MM size with MS flange, nuts, bolts and rubber gaskets etc. including its testing and cost of all Materials, Labours and T&P etc. as per direction of E/I.(ISI marked. Make- Kartar, Castle, Audco) ( NSI ) | BI01010001010000000000000515BI0100001218 | 15 | Nos | 4565 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 68475 | 68475 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | Supply, fixing and testing in position ISI marked and approved make cast iron wafer type non return valve including all interal fittings of 80mm size with MS flange, nuts, bolts and rubber gaskets etc. including its testing and cost of all Materials, Labours and T&P etc. as per direction of E/I. (ISI marked. Make- Kartar, Castle, Audco) ( NSI ) | BI01010001010000000000000515BI0100001219 | 8 | Nos | 3652 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 29216 | 29216 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | Supply and installation of two way 63mm instantaneous inlet for fire brigade connection including provision of cast iron Butter fly valve the cost of butter fly valve shall be under separate item and making connection with 100NB fire fighting pipe, painting with fire red paints completing the work in all respect as per the direction of E/I Make- New age, Padmani, Guard, HS. ( NSI ) | BI01010001010000000000000515BI0100001220 | 9 | Nos | 10780 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 97020 | 97020 | #VALUE!
17 | Supply, fixing, testing and commissioning of single headed 63 mm dia gunmetal/S.S. landing hydrant valve flanged inlet with 63 mm female instantaneous outlet confirming to IS 5290 on the fire wet riser down comer including making 80NB pipe connecting with riser fixing the landing hydrant valves in proper position and alignment including supply of nuts, bolts ,gasket and caps chain etc and testing of the hydrant including cost of all Materials, Labours and T&P etc. as per direction of E/I.(Make- Newage,Padmani, Getech, HS). NSI | BI01010001010000000000000515BI0100001221 | 11 | Nos | 7590 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 83490 | 83490 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Supply, fixing, testing and commissioning of 20mm dia bore and 30 meter long hose rubber lined Dunlop pipe and hose reel for first aid fire fighting confirming to IS 384 with full swing drum fixing brackets 5 mm dia shut off gunmetal brass nozzle 25 mm dia globe valve connection to the landing valve through adopter or directly from the riser through 25 mm dia GI pipe as required including 25 mm dia pipe length with all sockets, elbows and nipples etc. including providing and operating instruction on a metal plate and fixing it near hose reel The system shall be complete in all respect as per drawing including cost of all Materials, Labours and T&P etc. as per direction of E/I.(Make- Newage,Padmani, Guard, HS). ( NSI ) | BI01010001010000000000000515BI0100001222 | 19 | Nos | 8525 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 161975 | 161975 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | Providing and fixing gun metal /S.S. ISI marked 63 mm dia branch pipes and 20 mm dia nozzle as per IS 903 of approved make and quality as required. including cost of all Materials, Labours and T&P etc. as per direction of E/I.( Make- HS,Newage, Superex, Padmani) ( NSI ) | BI01010001010000000000000515BI0100001223 | 4 | Nos | 3267 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 13068 | 13068 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | Providing and fixing ISI Marked fire RRL hose pipe 15 meter long and 63 mm dia with ISI marked IS 903 gun metal male and female coupling of approved make and quality as required near wet riser including cost of all Materials, Labours and T&P etc. as per direction of E/I. (Make- CRC, Newage, Padmani,HS). ( NSI ) | BI01010001010000000000000515BI0100001224 | 6 | Nos | 6567 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 39402 | 39402 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | Providing and fixing Hose cabinet box size 600X750X250MM made of 16 gauge M.S sheet duly painted with PO red paint 03 coats with central 6mm thick glass door, lock handle and fixing support on wall Including cost of all Materials, Labours and T&P etc. as per direction of E/I. ( NSI ) | BI01010001010000000000000515BI0100001225 | 3 | Nos | 5885 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 17655 | 17655 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | Supply, fixing, testing & commissioning of electrical motor driven fire pump suitable for automatic operation of following jockey pump.(Make- Kirloskar, Crompton Model No.DB 32/20) (a) Horizontally mounted centrifugal fire pump complete for delivery of 150 LPM against a total head of 45 meter with necessary pressure gauge of approved make including by pass arrangement for periodic testing of the working of the pump set. The pump casing shall be of cast iron, impeller shall be of bronze and shaft shall be stainless steel (b) Squirrel cage TEFC induction motor (2900 RPM) Crompton/Kirloskar/ABB as per IS 325-1978 suitable for 415 volt 3 phase 50 HZ (5 HP) for the above pump and flexible coupling with the pump. (c) Common bed plate of fabricated mild steel channel or cast iron type. (d) Suitable cement concrete pump foundation and vibration clamping arrangement as required. (e) Pressure switch for pump for automatic operation including necessary wiring up to control panel. NSI | BI01010001010000000000000515BI0100001226 | 2 | Nos | 62535 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 125070 | 125070 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
23 | Supply, fixing, testing & commissioning of Diesel engine driven fire pump suitable for automatic operation consisting of following for hydrant system. (Make- kirloskar) (a) Horizontally mounted centrifugal fire pump model No DB/65/32 complete for delivery of 1000 LPM against a total head of 35 meter so as to ensure a minimum pressure of 35 meter at highest and farthest outlet at the specified flow complete with necessary pressure gauge including by pass arrangement for periodic testing of the working of the pump set. The pump casing shall be of cast iron, impeller shall be of bronze and shaft shall be stainless steel. (b) Squirrel cage, TEFC induction diesel engine Model DA-20,kirlosker 20BHP for the above pump and flexible coupling with the pump with 1500 RPM (c) Common bed plate of fabricated mild steel channel or cast iron type. (d) Suitable cement concrete pump foundation and vibration clamping arrangement as required. (e) Pressure switch for automatic operation of motor including necessary wiring up to control panel. ( NSI ) | BI01010001010000000000000515BI0100001227 | 1 | Nos | 320771 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 320771 | 320771 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
24 | Supply, installation, testing and commissioning of standard Fireman's Axe (tested for 20000 Volts) with heavy insulated rubber handle (ISI marked). NSI | BI01010001010000000000000515BI0100001228 | 4 | Nos | 970 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3880 | 3880 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | Supply, installation, testing and commissioning of CI Ball Valve, 25mm dia, "KARTAR" make (For Hose Reel). NSI | BI01010001010000000000000515BI0100001229 | 4 | Nos | 1150 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4600 | 4600 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
26 | Supply, Installation, testing & commissioning of single plate Non Return Valve, 150 mm dia, ISI marked, “KARTAR” make with fittings viz. flange, nut-bolt & rubber insertion etc. NSI | BI01010001010000000000000515BI0100001230 | 4 | Nos | 4285 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 17140 | 17140 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | Supply, installation, testing and commissioning of Pressure Switch, IPS 100, “INDFOS” make 0 to 7 bar (Adustable) with socket, nipple, ball valve etc. (One each for Main Electrical, Diesel Engine driven & Jockey Pump at delivery). NSI | BI01010001010000000000000515BI0100001231 | 4 | Nos | 2625 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10500 | 10500 | #VALUE!
28 | Supply, installation, testing and commissioning of Water cum Foam Monitor, 63mm dia “WIMCO/ NEWAGE/ HD” make complete with aluminum nozzle, made out of seamless hot dip galvanized pipe and gun metal couplings having locking arrangement etc. capable of moving to any direction in 360 degree angle horizontally and 105 degree angle vertically with Reqired siz Butterfly Valve, matching flanges, nut bolt etc. (Note: cost oo butter fly Valve is in the separate item), pressure 20 bar , LPM 1750 or more. NSI | BI01010001010000000000000515BI0100001232 | 2 | Nos | 23500 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 47000 | 47000 | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
29 | Supply, installation, testing and commissioning of gun metal single acting Air Release Valve (Spring loaded)with screwed inlet 25mm dia. Make "KARTAR" K616 or eqivqlent. NSI | BI01010001010000000000000515BI0100001233 | 2 | Nos | 3425 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6850 | 6850 | #VALUE!
30 | Supply, installation, testing and commissioning of 01 Inch stainless steel FB5X Foam making nozzle for pipe size 100mm dia SS grade 304W, flow rate 225 LPM, Length 455 mm and working pressure 8kgf/Sqcm. NSI | BI01010001010000000000000515BI0100001234 | 2 | Nos | 4200 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8400 | 8400 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
31 | Supply, installation, testing and commissioning of Foam chemical, AFFF- 6%, ISI marked, IS: 4989, "FIRECHEM" Make (Available in 20 ltrs. Capactiy PVC drum). NSI | BI01010001010000000000000515BI0100001235 | 2 | Nos | 110 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 220 | 220 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
32 | Supply, installation, testing and commissioning of CIDF Sluice Valve, 150mm dia, “KALPANA or KIELOSKAR” brand, ISI marked, Cat No NRSV P.N. 1.0 (12CR12-GM-IS Flanged FF IS 1538 Tbl 4&6 cast Iron body & Wedge Shaft: 12CR12, boady and Wedgw seat: Bronze, Hand operated Wheel operation with flange, nut-bolts & rubber insertion. (At suction). NSI | BI01010001010000000000000515BI0100001236 | 2 | Nos | 23800 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 47600 | 47600 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
33 | Supply, installation, testing and commissioning of Water cum Foam Monitor, 100mm dia “WIMCO/ NEWAGE/ HD” make complete with aluminum nozzle, made out of seamless hot dip galvanized pipe and gun metal couplings having locking arrangement etc. capable of moving to any direction in 360 degree angle horizontally and 105 degree angle vertically with 100mm Butterfly Valve, matching flanges, nut bolt etc. (Note: cost of 100mm butter fly Valve is in the separate item), flow 7Kg/Sqcm, LPM 3750 or more. NSI | BI01010001010000000000000515BI0100001237 | 1 | Nos | 30270 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 30270 | 30270 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
34 | Supply, installation, testing and commissioning of Mild steel FB5X Foam making branch pipe, 150 PSI, size standard. NSI | BI01010001010000000000000515BI0100001238 | 2 | Nos | 8270 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 16540 | 16540 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
35 | Supply, installation, testing and commissioning of Electric Motor Driven 40 H.P Fire pumping set suitable for automatic operation consisting of the following as per specifications (Make Kirlosker, Crompton) Pump Model DB-80/20:(a) Horizontally mounted, centrifugal type single fire pump having cast iron body, gunmetal/ bronze impeller, stainless steel shaft and capable of delivering 97 m3/ hr (1620 LPM) against a total head of 70 Mtrs. (b) Squirrel cage induction motor totally enclosed fan cooled type suitable for 400/400 volts (+5%) 3 phase, 50 Hz. A. C. supply of suitable capacity of not less than 40 HP for the above pump with synchronous speed of 2900 RPM confirming to IS: 325 and duly coupled with above pump with flexible coupling including earthing as per relevant Indian standard and specifications (c) Common bedplate for mounting pump and motor fabricated of suitable M.S. channel as per manufacturer’s recommendations. NSI | BI01010001010000000000000515BI0100001239 | 1 | Nos | 172700 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 172700 | 172700 | #VALUE!
36 | Supply, installation, testing and commissioning of cubical type floor mounted fire pump control panel fabricated from 16 Gauge M.S. sheet duly painted with stove enameled finish of approved make & shade and comprising of: (a) One incoming 250 ampere MCCB switch unit with 250 AMP MCCB AMP Tpn Busbar Volt metre, volt meter, selector switch and indication lights. (b) One 250 AMP MCCB unit with 63 AMP HRC fuses. (c) One 63 AMP MCCB unit with 63 AMP MCCB. (d) One fully automatic star delta starter suitable for main pump with overload relay, timer, push buttons and auto manual selector switch.(e) One fully automatic direct on line starter suitable for motor with O/L relay, Push Button and Auto/ manual selector switch. (f) Three phase indicating lamps. (g) Three panel type ampere meters one for each motor with ASS, CTS etc. (h) Three neon indication lamps. (i) Fully automatic diesel engine starting system with battery charger, indicating lights, transformer, rectifier, timer, voltmeter, Amp. Meter, selector switches, push buttons, auxiliary relay etc. NSI | BI01010001010000000000000515BI0100001240 | 1 | Nos | 151000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 151000 | 151000 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
37 | Supply, installation, testing and commissioning of Pressure Gauge, stainless steel, Glycerin filled, 100mm dia 0-10 kg./cm2 “TIPCO/H-GURU” make with socket, nipple, ball valve, U tube etc. (One each for Main Electrical, Diesel Engine driven & Jockey Pump at delivery). NSI | BI01010001010000000000000515BI0100001241 | 5 | Nos | 1890 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9450 | 9450 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
38 | Fabrication, supply, fixing, testing & commissioning of cubical type flow mounted electrical control panel box size 1100mmx900mmx300mm of 2mm thick CRCA sheet for fire fighting pumps with suitable relays. MCCB for incoming and outgoing contactor star delta starter , indication lamps, ammeter, voltmeter, selector switches and indication lights for incoming and outgoing feeder, auxiliary switches dry suction cut off single phase preventer cooper bus bar etc. The panel shall be provided with interlocking arrangement between electric motor driven pumps so that only one pump can operate one time the installation shall be complete including all control wiring and connection as required for flowing pump one no Diesel motor pump and one no jockey pump. As per direction of E/I. NSI | BI01010001010000000000000515BI0100001242 | 1 | Nos | 63800 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 63800 | 63800 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
39 | Providing and fixing of 6 Sq mm FR PVC insulated 1100 V grade 3 core copper cable of approved make and quality including its connection to main switch board & electric motor etc complete with testing as per direction by E/I. NSI | BI01010001010000000000000515BI0100001243 | 200 | RM | 182 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 36400 | 36400 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
40 | Supply, Installation, testing & commissioning of Butter Fly Valve, 100 mm dia, P. N. 1.0 “KARTAR” make, ISI marked, IS: 13095 complete with all fittings viz. Flanges, gasket, nut-bolts etc. NSI | BI01010001010000000000000515BI0100001244 | 4 | Nos | 5950 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 23800 | 23800 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
41 | Supply, Installation, testing & commissioning of Butter Fly Valve, 150 mm dia, P. N. 1.0 “KARTAR” make, ISI marked, IS: 13095 complete with all fittings viz. Flanges, gasket, nut-bolts etc. NSI | BI01010001010000000000000515BI0100001245 | 4 | Nos | 8020 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 32080 | 32080 | #VALUE!
42 | Supply, installation, testing and commissioning of Four way Fire Brigade Inlet, “NEWAGE” make cast iron comprising of 63mm gun metal instantaneous male inlet coupling with plug and cap chain as per IS: specification with flange, nut bolt, rubber gasket etc. NSI | BI01010001010000000000000515BI0100001246 | 2 | Nos | 15400 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 30800 | 30800 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
43 | Supply, fixing and testing in position ISI marked and approved make cast iron dual plate wafer type non return valve (check valve) including all interal fittings of 150 mm size with MS flange, nuts, bolts and rubber gaskets etc. including its testing and cost of all Materials, Labours and T&P etc. as per direction of E/I. (ISI marked. Make- Kartar, Castle, Audco). NSI | BI01010001010000000000000515BI0100001247 | 4 | Nos | 8640 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 34560 | 34560 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
44 | Supply, fixing and testing in position ISI marked and approved make cast iron wafer type non return valve including all interal fittings of 100 mm size with MS flange, nuts, bolts and rubber gaskets etc. including its testing and cost of all Materials, Labours and T&P etc. as per direction of E/I. (ISI marked. Make- Kartar, Castle, Audco) . NSI | BI01010001010000000000000515BI0100001248 | 4 | Nos | 5715 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 22860 | 22860 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
45 | Supply, installation, testing and commissioning of Manual Call Point, break glass type The call points should comprises of push button of reputed make enclosed in ABS box with M.S. chain and hammer. The push button will have one pair of normally open and one pair of close contacts. The push button would be on non-shrouded construction. The whole assembly of the push button in ABS box is enclosed on the external ABS front cover, which will be seated in the front means of breakable glass with neoprene gasket. Under normal conditions push button would be in depressed condition so long the front glass cover is broken. The push button will be released by the spring action that should give remote Fire alarm through the contacts. “AGNI” make or Palex.NSI | BI01010001010000000000000515BI0100001249 | 4 | Nos | 1329 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5316 | 5316 | #VALUE!
46 | The Detector is backward compatible with the Series 100 detector bases, thus providing the capability to upgrade, extend and maintain existing Series 100 installations. The detector incorporates a bi-colour LED indicator. The integral LED changes colour according to the detector’s status - Green = Normal, Red = Alarm. This benefits the user by providing clear, instant visual indication of the detector’s condition. Drift compensation’ algorithms are one of the key features of the detector. These algorithms ensure a consistent alarm sensitivity threshold for periods between service intervals. This provides the user with both a reduction in the frequency of nuisance alarms and maintenance savings by extending the period. NSI | BI01010001010000000000000515BI0100001250 | 4 | Nos | 2475 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9900 | 9900 | #VALUE!
47 | Supply, installation, testing & commissioning of Air Cushion Tank with air release valve, pressure gauge, drainpipe, drain valve. The air cushion tank shall be made of 250mm dia x 1.5 mtrs. long M.S. pipe 6mm thick, heavy duly C class with suitable stand for fixing on the ground. The air cushion tank shall be duly painted with two coats of red oxide primer & thereafter two coats of P.O. red enamel paint of reputed brand viz. “NEROLAC/ ASIAN / BERGER”. All necessary piping from the outlet of the pump to the air cushion tank shall also be done as per requirements. NSI | BI01010001010000000000000515BI0100001251 | 4 | Nos | 25250 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 101000 | 101000 | #VALUE!
48 | Supply, installation, testing and commissioning of Electronic Hooter with Flasher, 24 volt, DC operatable, made out of M.S. sheet heavy duty duly powder coated with epoxy powder coating, plastic body 500 mtrs. audible range with built in transformer etc. “AGNI” make. NSI | BI01010001010000000000000515BI0100001252 | 4 | Nos | 1375 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5500 | 5500 | #VALUE!
49 | Supply, Installation, testing & commissioning of single plate Non Return Valve, 100 mm dia, ISI marked, “KARTAR” make with fittings viz. flange, nut-bolt & rubber insertion etc. NSI | BI01010001010000000000000515BI0100001253 | 4 | Nos | 2560 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10240 | 10240 | #VALUE!
50 | Supply and fixing of submersible cable Havels or equivalent make, for submersible pump complete in all respect. c) 4.0 mm2 for pump above 3 HP and up to 7.5 H.P. (CSI No. 19.33(c)) | BI01010001010000000000000515BI0100001254 | 10 | RM | 130 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1300 | 1300 | #VALUE!
51 | Supply and fixing of submersible cable Havels or equivalent make, for submersible pump complete in all respect. d) 6.0 mm2 for pump above 7.5 HP and up to 15 H.P. (CSI No. 19.33(d)) | BI01010001010000000000000515BI0100001255 | 10 | RM | 185 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1850 | 1850 | #VALUE!
52 | Extraction of defective VT submersible pumps and motor with 60" x 90" column pipe and then lowering of the repaired pump and motor with pipe and testing the same including checking main cut-out fuse and operation of Tube well for 24 hours fo rits smooth working with all cost of materials,labour and T&P etc required for the proper completion of the work. (CSI No. 20.28) | BI01010001010000000000000515BI0100001256 | 1 | Job | 3944 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3944 | 3944 | #VALUE!
53 | S/F full way CI Gate valve of 63 mm dia. With wheel , BSI mark heavy quality including supply of all labour , material andT & P for proper completion of work . (CSI No. 28.02) | BI01010001010000000000000515BI0100001257 | 10 | Nos | 4524 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 45240 | 45240 | #VALUE!
54 | S/F full way 63/65 mm dia Fire hydrant Gun Metal Gate Valve heavy quality including supply of all labour , material andT & P for proper completion of work (CSI No. 28.03) | BI01010001010000000000000515BI0100001258 | 10 | Nos | 14328 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 143280 | 143280 | #VALUE!
55 | P/F Male & Female coupling 63/65 mm dia. Gun metal BSI marked confirming to IS:903 heavy quality including supply of all labour , material and T & P for proper completion of work (CSI No. 28.04) | BI01010001010000000000000515BI0100001259 | 10 | Nos | 5404 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 54040 | 54040 | #VALUE!
56 | P/F Short Branch pipe Gun Metal BSI marked heavy quality including supply of all labour , material and T & P for proper completion of work. (CSI No.28.05) | BI01010001010000000000000515BI0100001260 | 10 | Nos | 1554 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15540 | 15540 | #VALUE!
57 | P/F 63 mm dia RLL Hose Pipe heavy quality having length 15.0 m including supply of all labour , material andT & P for proper completion of work. (CSI No. 28.06) | BI01010001010000000000000515BI0100001261 | 90 | RM | 322 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 28980 | 28980 | #VALUE!
58 | P/F MS Hose Box Single Door with stand for 15 mt RRL Hose heavy quality including supply of all labour , material andT & P for proper completion of work. (CSI No. 28.07) | BI01010001010000000000000515BI0100001262 | 10 | Nos | 6278 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 62780 | 62780 | #VALUE!
59 | Placing of 10 KL PVC Tank over slab of 6 m staging including supply of all labour , material andT & P for proper completion of work.(CSI No.28.08) | BI01010001010000000000000515BI0100001263 | 10 | Job | 5280 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 52800 | 52800 | #VALUE!
60 | Cartage of ballast,Kankar,Coal grit or sand etc. including loading and unloading but excluding stacking at pucca roads. (i) For Ist Km CSI No.3.01 (a) | BI01010001010000000000000515BI0100001264 | 20 | Cum/Km | 136 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2720 | 2720 | #VALUE!
61 | Cartage of ballast,Kankar,Coal grit or sand etc. including loading and unloading but excluding stacking at pucca roads. (ii) 2nd & 3rd KM CSI No.3.01 (a) | BI01010001010000000000000515BI0100001265 | 20 | Cum/Km | 28 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 560 | 560 | #VALUE!
62 | Excavation in foundation in ordinary soil (loam, clay or sand) including lift upto 1.5 Metre and lead upto 30 metre including filling, watering, and ramming of excavated earth into the trenches or into the space between the building and the side of the foundation. CSI No. 4.01 | BI01010001010000000000000515BI0100001266 | 90 | Cum | 198 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 17820 | 17820 | #VALUE!
63 | Add to Earth work item (SI No. 4.01 to 4.03) for every additional 30m lead or part thereof or for every additional 1.5M lift or part thereof. (CSI No. 4.04) | BI01010001010000000000000515BI0100001267 | 90 | Cum | 30 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2700 | 2700 | #VALUE!
64 | Sand filling in plinth including supply of necessary quantity of fine sand from outside the UPPCL premises including watering, dressing etc. Rate to include cost of all materials, labour and T&P etc. required for proper completion of work. CSI No. 4.05 | BI01010001010000000000000515BI0100001268 | 14 | Cum | 2048 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 28672 | 28672 | #VALUE!
65 | Earth filling under floors and road including cost of the earth when obtained from outside Corporations area including its carriage loading unloading watering, ramming in 20cm layers and dressing of earth etc. Rate including cost of earth, labour ,T&P and ROYALITY etc.required for proper completion of work. CSI No. 4.10 | BI01010001010000000000000515BI0100001269 | 50 | Cum | 436 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 21800 | 21800 | #VALUE!
66 | Levelling and dressing and making proper slopes including cutting and filling of earth upto a depth 100mm if so required including all labour T&P etc. required for proper completion of the work. CSI No. 4.11 | BI01010001010000000000000515BI0100001270 | 50 | Sqm | 4 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 200 | 200 | #VALUE!
67 | Concrete with 4cm gauge stone ballast, coarse sand (F.M. 1.8 to 2.5) & cement in proportion of 12:6:1 in foundations &under floors including supply of all materials, labour and tools and plants etc. required for proper completion. CSI No. 5.02 | BI01010001010000000000000515BI0100001271 | 15 | Cum | 5820 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 87300 | 87300 | #VALUE!
68 | Cement concrete with 2cm gauge approved hard stone ballast, coarse sand (F.M. 1.8 to 2.5) and cement in proportion of 4:2:1 including supply of all materials, labour,side shuttering if required and T&P etc. required for proper completion of work. CSI No. 5.06 | BI01010001010000000000000515BI0100001272 | 2 | Cum | 7520 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15040 | 15040 | #VALUE!
69 | Cement concrete with 2cm gauge approved hard stone ballast, coarse sand (F.M. 1.8 to 2.5) and cement in proportion of 3:1.5:1 including supply of all materials, labour,side shuttering if required and T&P etc. required for proper completion of work. CSI No. 5.21 | BI01010001010000000000000515BI0100001273 | 2 | Cum | 7989 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15978 | 15978 | #VALUE!
70 | Precast cement concrete door sills, chaukhats boundary posts, shelves and similar small work with cement, approved coarse sand (F.M. 1.8 to 2.5) and 2 cm gauge graded approved hard stone ballast in the proportion 1:1.5:3, excluding reinforcement but including fixig the same in position including cost of all other material, labor and T&P . CSI No. 5.22 | BI01010001010000000000000515BI0100001274 | 2 | Cum | 9550 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 19100 | 19100 | #VALUE!
71 | RCC work with cement, approved coarse sand (F.M. 1.8 to 2.5) and 2 cm gauge graded approved hard stone ballast like granite, quartzite etc from Dalla, Jhansi or other quarries in proportion 1:1.5:3 in lintels of doors and windows, excluding supply of reinforcement & its bending but including its fixing and binding the same with binding wire, including cost of all other materials labour and T&P.. CSI No. 5.23 | BI01010001010000000000000515BI0100001275 | 2 | Cum | 9205 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 18410 | 18410 | #VALUE!
72 | RCC work with cement, approved coarse sand (F.M. 1.8 to 2.5) and 2 cm gauge graded approved hard stone ballast like granite, quartzite etc from Dalla, Jhansi or other quarries in proportion 1:1.5:3 in slab, excluding supply of reinforcement & its bending but including its fixing and binding the same with binding wire, including cost of all other materials labour and T&P CSI No. 5.24 | BI01010001010000000000000515BI0100001276 | 10 | Cum | 10600 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 106000 | 106000 | #VALUE!
73 | RCC work with cement, approved coarse sand (F.M. 1.8 to 2.5) and 2 cm gauge graded approved hard stone ballast like granite, quartzite etc from Dalla, Jhansi or other quarries in proportion 1:1.5:3 in lighter beams i.e. having span upto 6m, excluding supply of reinforcement & its bending but including its fixing and binding the same with binding wire, including cost of all other materials labour and T&P. CSI No. 5.25 | BI01010001010000000000000515BI0100001277 | 1 | Cum | 11473 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11473 | 11473 | #VALUE!
74 | RCC work with cement, approved coarse sand (F.M. 1.8 to 2.5) and 2 cm gauge graded approved hard stone ballast like granite quartzite etc from Dalla, Jhansi or other quarries in proportion 1:1.5:3 in raft foundation and footings , excluding supply of reinforcement & its bending but including its fixing and binding the same with binding wire, including cost of all other materials labour and T&P. CSI No. 5.27 | BI01010001010000000000000515BI0100001278 | 10 | Cum | 8801 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 88010 | 88010 | #VALUE!
75 | RCC work with cement, approved coarse sand (F.M. 1.8 to 2.5) and 2 cm gauge graded approved hard stone ballast like granite, quartzite etc from Dalla, Jhansi or other quarries in proportion 1:1.5:3 in RCC T beam-slab and column, excluding supply of reinforcement & its bending but including its fixing and binding the same with binding wire, including cost of all other materials labour and T&P. CSI No. 5.29 | BI01010001010000000000000515BI0100001279 | 23 | Cum | 11647 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 267881 | 267881 | #VALUE!
76 | First class brick work in 1:6 cement and coarse sand (F.M.1.8 to 2.5) mortar in foundation and plinth including supply of all materials, labour & T&P etc. required for proper completion of work. CSI No. 6.01 | BI01010001010000000000000515BI0100001280 | 10.7 | Cum | 4873 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 52141.1 | 52141.1 | #VALUE!
77 | First class brick work in 1:4 cement and coarse sand (F.M.1.8 to 2.5)mortar in foundation and plinth including supply of all materials, labour & T&P etc. required for proper completion of work. CSI No. 6.03 | BI01010001010000000000000515BI0100001281 | 1.5 | Cum | 5071 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7606.5 | 7606.5 | #VALUE!
78 | First class brick work in 1:6 cement and coarse sand mortar in super structure including necessary cutting and moulding of bricks as required and also including honeycomb brick work for wall of one brick thick (230mm) including supply of all materials, labour & T&P etc. required for proper completion of work. CSI No. 6.01+6.07+6.08 | BI01010001010000000000000515BI0100001282 | 17 | Cum | 5572 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 94724 | 94724 | #VALUE!
79 | First class brick (class-150) work in 1:4 cement and coarse sand (F.M. 1.8 to 2.5) mortar in super structure including necessary cutting and moulding of bricks as required and also including honeycomb brick work for wall of 1½ brick thick (115mm) including supply of all materials, labour & T&P etc. required for proper completion of work. CSI No. 6.03+6.07+6.09 | BI01010001010000000000000515BI0100001283 | 1 | Cum | 5931 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5931 | 5931 | #VALUE!
80 | Brick work in foundation & plinth with old dismantled bricks (supplied by department free of cost) and coarse sand of F.M. 1.8 to 2.5 mortar in 1:6 including supply of all other materials, labour, removing mortar & cleaning of old & used bricks,T&P etc complete. CSI No. 6.18 | BI01010001010000000000000515BI0100001284 | 2 | Cum | 2831 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5662 | 5662 | #VALUE!
81 | Mild Steel or Iron work in heavy sizes such as trusses built up gates, door frames, record, racks roof work gates etc. wrought to required form including holes rivetting or welding where necessary and also fixing in proper position and alignment including cost of all materials supplied by contractor. CSI No. 9.01 | BI01010001010000000000000515BI0100001285 | 1.1 | M.T. | 99064 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 108970.4 | 108970.4 | #VALUE!
82 | As in CSI No. 9.01 above but when steel is to be provided by the department. CSI No. 9.02 | BI01010001010000000000000515BI0100001286 | 0.5 | M.T. | 32734 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 16367 | 16367 | #VALUE!
83 | TMT/Tor steel in plain work such as reinforced concrete or reinforced brick work (when not included in an over all rates) wrought to required shape as necessary including bending for proper completion of the work and including supply of steel its wastage, bend, hooks and authorized overlapping shall be measured. (Steel shall be arranged by the contractor) CSI No. 9.03 | BI01010001010000000000000515BI0100001287 | 1.2 | M.T. | 88068 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 105681.6 | 105681.6 | #VALUE!
84 | As in CSI No. 9.03 above but when steel is provided by the Department. CSI No. 9.04 | BI01010001010000000000000515BI0100001288 | 0.8 | M.T. | 22785 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 18228 | 18228 | #VALUE!
85 | Supplying and fixing rolling shutters of approved make made of 80x1.25 mm. Gauge cold rolled M.S. lathes inter locked through out their inner length and joined together at the end by end lock guides & arrangements for inside and outside locking with push &pull operation complete but excluding the cost of top cover and springs. CSI No. 9.08 | BI01010001010000000000000515BI0100001289 | 2 | Sqm | 2311 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4622 | 4622 | #VALUE!
86 | P/F 27.5cm. long wire spring grades 2 for rolling shutters. CSI No. 9.09 | BI01010001010000000000000515BI0100001290 | 1 | Nos | 506 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 506 | 506 | #VALUE!
87 | Providing and fixing top cover rolling shutters. CSI No. 9.10 | BI01010001010000000000000515BI0100001291 | 3 | RM | 503 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1509 | 1509 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
88 | Providing & fixing ball bearing for rolling shutters. CSI No. 9.11 | BI01010001010000000000000515BI0100001292 | 2 | Nos | 561 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1122 | 1122 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
89 | Fabrication & supply and fixing of Tubular steel trusses duly painted with one coat of red oxide paint, designed & manufactured as per latest I.S.S. suitable for A.C. sheet roofing cover of the Store Shed.Thickness of Tubes shall not be less than 3.25 mm. Including cost of all materials, labour T&P etc. complete as required for proper completion of work & cartage upto site as per drawing including all accessories. CSI No. 9.16 | BI01010001010000000000000515BI0100001293 | 1.1 | M.T. | 86331 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 94964.1 | 94964.1 | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
90 | Supply and fixing galvanised mosquito proof jali (16x24 gauge) with M.S. flat of 20 x 3 mm. size, on both sides screwed or welded to window or door frame. CSI No. 9.18 | BI01010001010000000000000515BI0100001294 | 9.05 | Sqm | 729 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6597.45 | 6597.45 | #VALUE!
91 | Providing M.S. Frames work, rack etc for R.C.C. Trench covers and edging with M.S. angles and M.S reinforcement including cutting, bending and welding as per approved drawing. The rate is including cost of all labour, materials etc. as required for proper completion of the work. CSI No. 9.20 | BI01010001010000000000000515BI0100001295 | 0.1 | M.T. | 96402 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9640.2 | 9640.2 | #VALUE!
92 | S/F welded wire mesh size 75x25mm and rectangular made out of 10 SWG over M.S. angle frame with M.S. flat welded as required including cost of drilling holes, washer welding etc as required including cost of all material, labour and T&P etc. required for proper completion of work . except cost of M.S angle and flat. CSI No. 9.22 | BI01010001010000000000000515BI0100001296 | 10 | Sqm | 472 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4720 | 4720 | #VALUE!
93 | 12 mm thick plaster with cement mortar consisting of one part of cement & four part of coarse sand (1:4), minimum thickness not to be less then 10 mm including supply of all material, labour and T&P etc for proper completion of work. CSI No. 11.07 | BI01010001010000000000000515BI0100001297 | 45 | Sqm | 193 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8685 | 8685 | #VALUE!
94 | Add for extra labour and materials for plaster over rough face of one brick thick wall. (CSI No. 11.12) | BI01010001010000000000000515BI0100001298 | 2 | Sqm | 26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 52 | 52 | #VALUE!
95 | 4.0 cm thick 1:2:4 plain cement concrete floor with cement, approved coarse sand & 2cm graded approved stone ballast laid in panels finished with 3mm floating coat of neat cement or cement and marble dust in ratio of 5:1 as specified and removing any overlapping mortar at the joints of the panels if any and giving them a uniform finish including supply of all materials, labour and T&P etc, required for proper completion of the work. without base CC. (CSI No. 12.04) | BI01010001010000000000000515BI0100001299 | 5 | Sqm | 414 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2070 | 2070 | #VALUE!
96 | Supply and Laying 8 mm thick glazed floor tiles of Somany, Johnson or equivalent make, , laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete, including supply of all materials, labour and T&P etc. required for proper completion of the work. (CSI No. 12.11) | BI01010001010000000000000515BI0100001300 | 1 | Sqm | 1085 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1085 | 1085 | #VALUE!
97 | Providing and fixing glass strips of 3.15 mm thickness & 40mm depth in joints of floor and skirting at the time of laying floors, flush with floor level including supply of all materials, labour& T&P etc. required for proper completion of work. (CSI No. 12.14) | BI01010001010000000000000515BI0100001301 | 10 | RM | 33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 330 | 330 | #VALUE!
98 | Providing (12x15) mm section groove in plaster including all material, labour and T&P etc. required for proper completion of the work. (CSI No. 11.16) | BI01010001010000000000000515BI0100001302 | 1.4 | RM | 12 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 16.8 | 16.8 | #VALUE!
99 | 3 mm thick floating coat of neat cement finish including supply of all materials,labour and T&P etc. required for proper completion of the work.( cement consumption 0.044 bag/Sq.m.) (CSI No. 11.20) | BI01010001010000000000000515BI0100001303 | 1 | Sqm | 21 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 21 | 21 | #VALUE!
100 | Supply of 80 mm thick I shaped mechanically compressed inter locking cement concrete paver block manufactured by high pressure & controlled vibration machine having plan dimension 200X(160+120 mm) with minimum 5 mm thick toping of O.P.Cement mixed with 25% marble powder. The compressive strength of concrete pavers blocks shall not be less than 30 MPa & 4.5 Kg/No. including cost of all material, labour, T&P etc. required for proper completion of work as directed by Engineer-in-charge but excluding G.S.T. which shall be paid extra as per rules. (CSI No.12.23) | BI01010001010000000000000515BI0100001304 | 56 | Sqm | 1029 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 57624 | 57624 | #VALUE!
101 | Painting or varnishing new iron work in small areas or new wood work with one coat of ready mixed priming paint and one coat of approved superior quality ready mix paint "Luxol" or equivalent brand or varnish including supply of all materials, labour and T&P etc. required for proper completion of the work. Paint to be used should conform to the I.S. 103-1950. (CSI No. 13.01) | BI01010001010000000000000515BI0100001305 | 50 | Sqm | 77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3850 | 3850 | #VALUE!
102 | As in item 13.01 above but for every coat after first coat. (CSI No. 13.02) | BI01010001010000000000000515BI0100001306 | 50 | Sqm | 36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1800 | 1800 | #VALUE!
103 | Same as CSI no. 13.01 above but every coat on previously painted old wood or steel work. CSI No. 13.03 | BI01010001010000000000000515BI0100001307 | 50 | Sqm | 49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2450 | 2450 | #VALUE!
104 | One priming coat and one coat oil bound distemper on new work including supply of all materials,labour and T&P etc. required for proper completion of the work. (CSI No. 13.08) | BI01010001010000000000000515BI0100001308 | 100 | Sqm | 69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6900 | 6900 | #VALUE!
105 | As in item 13.08 but for every coat after the first coat. (CSI No. 13.09) | BI01010001010000000000000515BI0100001309 | 100 | Sqm | 28 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2800 | 2800 | #VALUE!
106 | Same as CSI No.13.08 above but for every coat on previously old distempered surface. CSI No. 13.10 | BI01010001010000000000000515BI0100001310 | 50 | Sqm | 35 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1750 | 1750 | #VALUE!
107 | Applying Birla or equivalent putty on new interior or exterior surface over one coat of water based cement primer of ICI or equivalent brand for smoothening and levelling of the surface as per requirement and direction of Engineer I/C including cost of all material, labour, T & P etc required for proper completion of work. (CSI No. 13.20) | BI01010001010000000000000515BI0100001311 | 100 | Sqm | 89 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8900 | 8900 | #VALUE!
108 | Painting one coat with APEX or equivalent brand weather coat paint on new wall surfaces (well prepared with Birla putty and one coat of primer ICI or equivalent which shall be paid separately) including through washing with water including cost of all materials, labour, T&P required for proper completion of work. (CSI No. 13.22) | BI01010001010000000000000515BI0100001312 | 50 | Sqm | 98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4900 | 4900 | #VALUE!
109 | Same as in item no 13.22 above but for every coat of additional APEX or equivalent brand weather coat paint . (CSI No. 13.23) | BI01010001010000000000000515BI0100001313 | 51 | Sqm | 44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2244 | 2244 | #VALUE!
110 | Same as CSI no13.22 above but for every coat of additional APEX or equivalent brand weather coat paint coat paint previously treated surface. CSI No. 13.24 | BI01010001010000000000000515BI0100001314 | 50 | Sqm | 65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3250 | 3250 | #VALUE!
111 | Dismantling brick work or stone work in lime or cement mortar and including stacking of materials as directed by the Engineer-in-charge within a distance of 60 metres. (CSI No. 15.01) | BI01010001010000000000000515BI0100001315 | 2 | Cum | 583 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1166 | 1166 | #VALUE!
112 | Dismantling reinforced cement concrete or reinforced brick work, including stacking of dismantled materials as directed by the Engineer-Incharge within a distance of 60 metres. (CSI No. 15.03) | BI01010001010000000000000515BI0100001316 | 1 | Cum | 1293 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1293 | 1293 | #VALUE!
113 | Dismantling cement concrete or brick or granolithic floors including base concrete and including stacking of dismantled materials as directed by the Engineer In-charge within a distance of 60 metres. (CSI No. 15.05) | BI01010001010000000000000515BI0100001317 | 5.9 | Sqm | 67 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 395.3 | 395.3 | #VALUE!
114 | Supply and laying 1.5 Sq.mm gauge copper wire of "Plaza" or equivalent make of approved quality including connecting with existing wiring in existing P.V.C.pipe. including all materials, labour and T&P complete.CSI No. 22.06 a | BI01010001010000000000000515BI0100001318 | 5.5 | RM | 74 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 407 | 407 | #VALUE!
115 | Supply and laying 2.5 Sq.mm gauge copper wire of "Plaza" or equivalent make of approved quality including connecting with existing wiring in existing P.V.C.pipe. including all materials, labour and T&P complete..CSI No. 22.06 b | BI01010001010000000000000515BI0100001319 | 10 | RM | 96 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 960 | 960 | #VALUE!
116 | Providing and fixing full way 25 mm dia G.M. gate valve with wheel, ISI mark heavy quality including supply of all materials, labour and T&P required for proper completion of work. (CSI No. 26.04-c) | BI01010001010000000000000515BI0100001320 | 7 | Nos. | 1371 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9597 | 9597 | #VALUE!
117 | Providing and fixing full way 50mm dia G.M. gate valve with wheel, ISI mark heavy quality including supply of all materials, labour and T&P required for proper completion of work. (CSI No. 26.04-f) | BI01010001010000000000000515BI0100001321 | 5 | Nos. | 2361 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11805 | 11805 | #VALUE!
118 | Supply and fixing of Syntex or equivalent make water storage tank including all materials, labours, T&P etc required for proper completion of work. (CSI No. 26.12) | BI01010001010000000000000515BI0100001322 | 500 | Lit | 11 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5500 | 5500 | #VALUE!
119 | Providing and fixing of 110 mm dia PVC pipe 6 Kg/ Sq.cm for with special such as Tee, bend, socket, elbow etc including supply of all labour,material,T & P etc complete required for proper completion of work. (CSI No. 26.17) | BI01010001010000000000000515BI0100001323 | 17 | RM | 294 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4998 | 4998 | #VALUE!
120 | Supply & Fixing high tensile steel colour coated Anti rust, high temp resistant sheet with tensile strength 550 PMA hot dip metallic (Zinc Aluminum) alloy (Nn-55%) Al, (45%) coating 70 GSM with total thickness not less than 0.45 mm (TCT) durashine or equivalent make with necessary over laps incl. S/F galvanized J/V hook with bolts, nuts, washer and bitumen washers etc. including cost of material, labour T&P etc. required for proper completion of work as per direction of E/I confirming I.S. 1397 : 1993. (Old Sor 2020 26.60) | BI01010001010000000000000515BI0100001324 | 18 | Sqm | 885 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15930 | 15930 | #VALUE!
Total in Figures | [51 empty] | 4999088.45 | #REF! | #VALUE!
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Note on K13: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information