## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-I, Noida
Name of Work: DETAILS OF WORK AND QUANTITY AGAINST E-TENDER NO. 144/EUDC-I/2023-24/NOIDA (WORKS) FOR CARRYING OUT THE 9 NOS. WORK IN HEAD SYSTEM STRENGTHENING / REPLACEMENT OF DAMAGED POLE / PANEL / ACB / FENCING / PLINTH / FUSE SET / EARTHING AS PER DPR S.NO. 1,2,3,4,5,6,7,8,9 IN AREA OF EUDSD-I/IV, NOIDA UNDER EUDD-I, NOIDA IN THE JURIDICTION OF EUDC-I, NOIDA (BUSINESS PLAN F.Y. 2024-25 RS. 33.51 CRORE FOR NOIDA ZONE).
Contact No: 0120-2970431
The bidder quoted rate should be inclusive GST & all other taxes)
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) Note:- 1. The bidder quoted rate should be inclusive GST & all other taxes. 2. Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC. 3. Payment will be done after complete execution of work/ entire project & submission of executed estimate and after getting satisfactory report in all respect from concern SDO/JE.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder with GST & all other taxes Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 5 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 6 | 54 | 7
1 | Cartage of following material from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to various points site of work including loading and unloading at both ends : - | BI01010001010000000000000515BI0100001138 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | 11 KV Comp. Poly. Pin Insulator with pin. | BI01010001010000000000000515BI0100001139 | 116 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.02 | 11 KV Disc Insulator T&C type 4500 kg. | BI01010001010000000000000515BI0100001140 | 35 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.03 | 11 KV Disc fitting. | BI01010001010000000000000515BI0100001141 | 30 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.04 | 11 KV D.O. Fuse Set. | BI01010001010000000000000515BI0100001142 | 78 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.05 | MS channel 125x65x1300mm (T-off). | BI01010001010000000000000515BI0100001143 | 32 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.06 | Earthing Complete | BI01010001010000000000000515BI0100001144 | 80 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.07 | ST Pole 13 Mtr. long SP-70 | BI01010001010000000000000515BI0100001145 | 80 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2 | Providing & fixing of following material of standard make / best quality for complete the work of pole structure at HT / LT line as per RESPO norms by the contractor at his own cost : - | BI01010001010000000000000515BI0100001146 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.01 | Clamp with nut & bolts for ST Pole | BI01010001010000000000000515BI0100001147 | 92 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.02 | F-Bracket with nut & bolts | BI01010001010000000000000515BI0100001148 | 30 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.03 | Stone Pad 300x300x75mm. | BI01010001010000000000000515BI0100001149 | 30 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.04 | LT Shackle Insulator. | BI01010001010000000000000515BI0100001150 | 150 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.05 | Al. crimping lug 70 Sq.mm. for connection on fuse set T/Fs. | BI01010001010000000000000515BI0100001151 | 702 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.06 | Al. lug ling barrel, off size (LS) 240 Sq.mm. | BI01010001010000000000000515BI0100001152 | 270 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
6 | Removal of conductor from both side spans of damaged pole and removal of H.T/L.T. line accessories from damaged pole. | BI01010001010000000000000515BI0100001153 | 80 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7 | Digging of pit of damaged pole in Pakka road (Hard soil) with the help of road cutter/digging machine, Tractor etc. for dismantling the pole. | BI01010001010000000000000515BI0100001154 | 80 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
8 | Erection of S.T. pole 11 Mtr. including fitting of all reqired accessories of HT/LT line as per RESPO schedule. | BI01010001010000000000000515BI0100001155 | 80 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9 | Grouting & concreting of each pole (In ratio of 1:4:8 in Cement, sand and Brick Ballast) in size 450mmx450mmx1800 mm as per RESPO schedule Complete in all respects. | BI01010001010000000000000515BI0100001156 | 80 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10 | Construction of Plinth in size 450x450x300 mm of each (0.880 Cu.m) pole above the ground level (In ratio of 1:3:6 in Cement, sand and Brick Ballast) as per RESPO schedule Complete in all respects. | BI01010001010000000000000515BI0100001157 | 80 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
11 | Excavation of earth and driving of M.S. earthing rod of size 20x2500 mm in earth and jointing through G.I wire of 6 SWG between support and earth electrode by providing proper size of bolts and nuts etc. as per RESPO schedule Complete in all respects. | BI01010001010000000000000515BI0100001158 | 80 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
12 | Re-laying and resagging of conductor in both side spans of erected pole in H.T/L.T line. | BI01010001010000000000000515BI0100001159 | 80 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | Fabrication & fixing of MS channel 125x65x1300mm (T-off) in all respects. | BI01010001010000000000000515BI0100001160 | 32 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
14 | Fixing of 11 KV D.O. Fuse Set. | BI01010001010000000000000515BI0100001161 | 78 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
15 | REPLACEMENT OF OLD & DAMAGED LT FEEDER PILLER OF VARIOUS SECTORS AS PER FOLLOWING :- | BI01010001010000000000000515BI0100001162 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
15.01 | Supply of new L.T. Feeder Pillar as per following specification with all relevant certificate :- 1) LT Feeder Pillar Box (Branch Distribution Pannel) shall be of 14 SWG HR sheet, having (1) doors in front of 14 SWG HR sheet. Doors should have proper locking arrangements with providing crome locks of standard make. It should have a canopy on top in order to prevent it from water ingress in rains. The doors of box should be welded with robust quality hinges and PVC GaskEt with provision of 3 hinges on each door and handle on each door with PVC Gasket. The periphery of door of the LT Feeder Pillar Box (Branch Distribution Pannel) shall be provided with lining of rubber/ PVC to prevent entry of rain, insects, lizards, rats etc. so as to make it vermin proof. 2) The dimension of Feeder Pillar Box (Branch Distribution Pannel) 4(Height) X 2.5(Width) X 2(Depth) Feet (With Canopy). 3) 04 Nos. Bus Bar insulation coated fo size 600x50x10mm. made of aluminum for red, yellow, blue & neutral phases suitable for 400 Amp. 4) 01 No. MCCB of 800 Amp. of L&T / Havell’s / ABB make for disconnecting of Supply. 5) 24 Nos. KIT KAT Fuse of 415V, 100 Amp. each capacity tested as per IS shall be provided with 8 Nos. on each phase so as to cater to 8 Nos. 3 Phase connections of conusmer. 6) Aluminum crimping lugs of size 400 / 240 / 120 / 95 / 70Sq.mm. and proper size thimbles shall be provided for safe termination of incomer as well as individual service cable as per qty. requirement. 7) Bakelite sheet shall be provided on the base of channel meant for mounting the Kit Kats. 8) All nuts, bolts & washers used shall be electro galvanized. 9) The height of erected feeder pillar box (Branch Distribution Pannel) approx. 2 feet from the earth on powder coating base of angle iron size 40x40x5mm frame with 04 nos. legs of 3 feet each (1 feet grout of angle on earth bottam, 1.6 feet grout in plinth and 6 inch gap in pannel base and plinth) 10) Grouting & Plinth of Feeder Pillar Box (Branch Distribution Pannel) as per site requirement complete in all respects. 11) The panel case consisting of door and roof (canopy) shall be powder coated with chemical process (weather proof) of Off-white color (Or as per direction) both inside and outside. Before painting, the sun faces shall be thoroughly cleaned from dust, grease and rust. Ientification no. shall be written as per direction. 12) Sundry item. | BI01010001010000000000000515BI0100001163 | 32 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
15.02 | Disconncetion of all Consumer connection from pannel as per requirement. | BI01010001010000000000000515BI0100001164 | 32 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
15.03 | Reconncetion of all Consumer connection from pannel after replacement as per requirement. | BI01010001010000000000000515BI0100001165 | 32 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
15.04 | Installation of above new L.T. Feeder Pillar in place of damaged L.T. Feeder Pillar with grouting, plinth and required items complete in all respect. | BI01010001010000000000000515BI0100001166 | 32 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
15.05 | Dismantling of damaged OLD Feeder Pannel Box from earth on work site. | BI01010001010000000000000515BI0100001167 | 32 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
15.06 | Carriage of above dismantled Pannel from works site to JE store / central store & proper stacking with loading & unloading. | BI01010001010000000000000515BI0100001168 | 32 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16 | Providing and installation of LT ACB 630 Amp. with cabinet / structure (L&T, HPL, Schneider, ABB, Hevell's, PVVNL approved make) as per following specification with all relevant certificate :- | BI01010001010000000000000515BI0100001169 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
16.01 | 630 amp. 03 pole fixed manual ACB. | BI01010001010000000000000515BI0100001170 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.02 | Red/yellow/blue light indication | BI01010001010000000000000515BI0100001171 | 14 | Sets | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.03 | ON & OFF Indication | BI01010001010000000000000515BI0100001172 | 28 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.04 | Amp., Volt meter& energy meter digital | BI01010001010000000000000515BI0100001173 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.05 | Metering C.T 630/5A, | BI01010001010000000000000515BI0100001174 | 42 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.06 | Panel fabrication of size 1250mm x 900mm x 600 mm made of M.S sheet 14 gauge with powder coating with panel lock and key arrangement.(two nos). and additional locking arrangement seprately including providing hut type shape as per drg. | BI01010001010000000000000515BI0100001175 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.07 | Fabrication of aluminium bus-bar for each phases | BI01010001010000000000000515BI0100001176 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
16.08 | Incoming size 425 mm x 50mmx12 mm (twin) | BI01010001010000000000000515BI0100001177 | 112 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.09 | Out going size 720 mm x 50mm x 12 mm(twin) | BI01010001010000000000000515BI0100001178 | 112 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.1 | Neutral size 900mmx50mmx12 mm. | BI01010001010000000000000515BI0100001179 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.11 | Fabrication of pannel stand made of M.S Angle of size 900mm x 600mm x 500 mm as per drg. | BI01010001010000000000000515BI0100001180 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.12 | Assembly of above ACB, Indicators, Meters, Metering CT & bus bar arrangment in the panel, fitting the panel on Stand with nut and bolts with wiring etc. & grouting in ratio 1:4:8 with cement, coarse sand and brick blast. | BI01010001010000000000000515BI0100001181 | 14 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.13 | Providing and fixing of aluminium bus bar of size 300mmx60mmx12 mm on L.T side of T/F. | BI01010001010000000000000515BI0100001182 | 112 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.14 | Making all connections with ACB & Distribution T/F and commissioning the ACB complete in all respect. | BI01010001010000000000000515BI0100001183 | 14 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
17 | WORK OF PROVIDING AND FIXING OF 20 NOS. NEW WIREMESH FENCING OF 11/0.4 KV L.T. SUB-STATION INSTALLED AT ABOVE PLACE AS PER FOLLOWING (All Material provided by contractor for above work.) :- | BI01010001010000000000000515BI0100001184 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
17.01 | 1. Frames of size 12'X15'x6' for each fencing of LT Sub-stations. (All Material provided by contractor for above work.) 2. The fencing shall be fabricated out of MS angle iron of size 40x40x5 mm having 2 Nos. legs of 45 Cm. long in each frame duly welded and fixed with wire mesh of size 75mm 25mm, 10 SWG within the frame, pressed under MS flat of size 25x5 mm inside the angle iron on all four sides with the help of duly Welded along with cross bracing of 25x5 mm MS flat on every frame will be grouted in 1:2:4 cement mortar with cement, coarse sand 20 mm gauge stone ballast. 3. Every frame after Fabrication will be painted with one coat of red oxide and two coats of Green synthetic enamel paint of approved make after proper cleaning. 4. The above mentioned frame will be jointed with each other with 70 mm long MS flat of size 25x5mm by first class welding as per site. 5. Fabrication and providing of wire mesh fencing frame for gate of size 4’x6’. Fabricated as per above specifications with proper locking arrangement. | BI01010001010000000000000515BI0100001185 | 20 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
17.02 | Construction of boundry / toe wall in bottom of fencing in brick work cement mortar 1:6 (1 cement : 6 coarse sand) for link in the size of 0.22mx0.60m (0.30m in earth, 0.30m above ground level) including plaster in cement mortar 1:4 and finishing with water proof cement paint. (Approx construction 12 Mtrs. boundry / toe wall for each fencing of LT Sub-stations.) (All Material provided by contractor for above work) | BI01010001010000000000000515BI0100001186 | 20 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
18 | WORK OF MAKING 10 NOS. NEW PLINTHS DISTRIBUTION T/F IN PLACE OF FULLY DAMAGE PLINTH / CAHAIR AT VARIOUS PLACE AS PER FOLLOWING :- | BI01010001010000000000000515BI0100001187 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
18.01 | Unmounting of T/F from plinth disconnecting all connection work including loading, carriage & unloading from work site. | BI01010001010000000000000515BI0100001188 | 10 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
18.02 | Construction of new distribution T/F Plinth. The size of plinth shall be 2 Mtrs. long, 2 Mtrs. wide and height 1.5 Mtrs. from ground level with 15 CM thick top CC slab and MS channel 125x65mm. The above work includes Excavation of earth, laying of bring ballast pad for foundation brick work, CC and plastering and proper curing complete with all respects as per RESPO schedule. (All Material provided by contractor for above work.) | BI01010001010000000000000515BI0100001189 | 10 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
18.03 | Mounting of T/F on plinth making all connection work including loading, carriage & unloading from work site. | BI01010001010000000000000515BI0100001190 | 10 | Jobs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19 | PROVIDING AND INSTALLATION OF CHEMICAL EARTHING FOR ABOVE NEW L.T. FEEDER PILLAR, ACB AND DTs (WITH ALL MATERIAL AND LABOUR) AFTER INSTALLATION RESISTANCE SHOULD BE LESS THAN ONE OHM. AS PER FOLLOWING (The all material and labour shall be provided by the contractor with 12 month guarantee for resistance value less than one OHM.) :- | BI01010001010000000000000515BI0100001191 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
19.01 | Providing of earth elctrode for chemical earthing Pipe in pipe type proper hot deep galvanization dia 50 mm length 3 mtr - 32mm x 6mm terminal connection hole dia 8mm The cavity between the pipe & pipe is filled with conductive mixture - for hermetically filling inside the cavity i.e. between secondary conductor & primary conductor, crystalline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc the electrode should be sealed from both the ends. The outer pipe of the elctrode should be galavanized the characteristics of this compound is highly cnductive, non magnetic & non corrosive in G.I. Including providing of backfill compound each elctrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested for above new L.T. Feeder Pillar, ACB & DTs. | BI01010001010000000000000515BI0100001192 | 202 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19.02 | Providing and fixing of GI strip of size 50 mm x 6 mm suitable for above new L.T. Feeder Pillar, ACB & DTs. | BI01010001010000000000000515BI0100001193 | 2166 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19.03 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. | BI01010001010000000000000515BI0100001194 | 606 | Mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
20 | Dismantling of ST Pole off size (Old & used) on work site. | BI01010001010000000000000515BI0100001195 | 80 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
21 | Carriage of above dismantled pole from works site to JE store / central store & proper stacking with loading & unloading. | BI01010001010000000000000515BI0100001196 | 80 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
22 | Dismantling of 11 KV Pin Insulator with pin (Old & used) on work site. | BI01010001010000000000000515BI0100001197 | 90 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
23 | Carriage of above dismantled insulator from works site to JE store / central store & proper stacking with loading & unloading. | BI01010001010000000000000515BI0100001198 | 90 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24 | Dismantling of LT ACB damaged (Iron Scrap) on work site. | BI01010001010000000000000515BI0100001199 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | Carriage of above dismantled ACB from works site to JE store / central store & proper stacking with loading & unloading. | BI01010001010000000000000515BI0100001200 | 14 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information