## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-II, Noida
Name of Work : iw.kZ tek ;kstuk ds vUrxZr eSllZ esnkUrk uks,Mk ;wfuV vkWQ Xykscy gSYFk fy0] ,Q&16] lSDVj 50 uks,Mk dks 2500 dsoh, Hkkj ¼,poh&1½ nks vyx&vyx 33 dsoh Lora= *cs* ¼izkFkfed L=ksr 400@220@132@33 dsoh izkFkfed midsUnz lSDVj 123] uks,Mk ,oa lsdsUMjh L=ksr 132@33 dsoh izkFkfed midsUnz lSDVj 115] uks,Mk½ ds ek/;e ls fuxZr djus gsrq 02 ua0 ubZ 33 dsoh Hkwfexr ykbZu fuekZ.k ls lEcfU/kr dk;ZA
Contract No: SHORT TERM E-TENDER NO 13/EUDC-II NOIDA/2024-25
G.S.T. EXTRA AS APPLICABLE.
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) (Note:- Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC.) 2.The rate quoted by the tenderer shall be inclusive of all duties, taxes (except GST), fees, octroi and other levies, materials, any type of NOC, labour to & FOR transportation of material and labour charges etc. ALL TAXES INCLUSIVE IN QUOTED RATES EXCEPT GST. 3. The work is to be done on SEMI TURNKEY BASIS. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE per unit In Figures To be entered by the Bidder IN Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Safe Cartage of following centralised stock material from any of the Store Center of PVVNL Discom to work site including Loading from Store and safe unloading at site for Item No. 2 to 15 | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | 33KV HT Cable 3x300sqmm |  | 1 | Mtr | 100 |  |  | Excess(+) | 13500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | 33KV O/D Cable Box for 3x300sqmm Cable |  | 1 | No. | 100 |  |  | Excess(+) | 71 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | 33KV I/D Cable Box for 3x300sqmm Cable |  | 1 | No. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | 33KV Straight Through for 3x300sqmm Cable |  | 1 | No. | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | ACSR Dog Conductor |  | 1 | Mtr | 100 |  |  | Excess(+) | 500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | ST Pole 11Mtr Long |  | 1 | No. | 100 |  |  | Excess(+) | 72 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | 33KV Pin Insulator with Pin |  | 1 | No. | 100 |  |  | Excess(+) | 216 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | Earthing Complete |  | 1 | No. | 100 |  |  | Excess(+) | 72 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | MS Top Channel 125x65x3200mm |  | 1 | No. | 100 |  |  | Excess(+) | 36 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | MS Dropper channel 100x50x2600mm |  | 1 | No. | 100 |  |  | Excess(+) | 108 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | 3Phase 4 WireStatic TVM for 33KV Connection |  | 1 | No. | 100 |  |  | Excess(+) | 5 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | AMR |  | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | 33KV Pilfer Proof Metering Cubicle 400/1A |  | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | 33KV CT/PT Double Pole Unit Combine Unit 400/1Amp. |  | 1 | No. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | Errection of above Centralised material and Supply and errection of the below De-Centralised material for completing the works as per RESPO. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | Supply of 160mm OD PN-4-PE-80, 6" Dia Grade UV Stabilized HDPE Pipe.(PVVNL GTP APPROVED) |  | 1 | Mtr | 100 |  |  | Excess(+) | 13000 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Work of Cable Laying through Trenchless method with HDPE Pipe in pakka Road from 400KV Primary Sub-Station Sector 123, Noida to Medanta Noida, F-16. Sector 50, Noida. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | Fabrication and Errection of Sectional Double Pole Riser by ST Pole 11Mtr. Long for 33KV Line with proper grouting and concreting of pole and proper installation of required accessories as per RESPO norms with complete work in all respect. (all work in the scope of Contractor) Grouting of - In ratio of 1:4:8 in Cement, sand and Brick Ballast) in size 450mmx450mmx1800 mm and Construction of Plinth in size 450x450x300 mm of each (0.285 Cum) pole above the ground level (In ratio of 1:3:6 in Cement, sand and Brick Ballast) as per RESPO. |  | 1 | Job | 100 |  |  | Excess(+) | 20 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | Drilling of dia 220 mm in bores for Single Curcuit by trenchless method by horizontal boring machine at a depth of 1.50 mtrs to 2.50 mtrs. (as per site requirement) below the ground level at Kaccha/Pakka Road/Road Crossing/as per site requirement with complete work in all respect as per RESPO. |  | 1 | Mtr | 100 |  |  | Excess(+) | 6900 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | Laying and interconnecting of above HDPE Pipe PE-80, PN-6, DN-160mm, 6" dia by HDD trenchless method for HOSTING OF 33 KV 3x300sq.mm XLPE cable with complete work in all respect. |  | 1 | Mtr | 100 |  |  | Excess(+) | 6900 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | Laying, Hosting and commissiong of 33 KV 3x300sqmm XLPE Cable Single Ckt. Cable in HDPE Pipe in HDD trenchless method with complete work in all respect. |  | 1 | Mtr | 100 |  |  | Excess(+) | 6900 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
23 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop and making risers at double pole and re-filling of pits in proper manner with required material at kacha/pakka and hot mix road. (All Work and material in the scope of contractor) |  | 1 | Nos. | 100 |  |  | Excess(+) | 20 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
24 | Laying of 33KV 3x300 Sq.mm XLPE Cable in the air on cable Riser Double Pole, existing trench cable trench, G.I.Pipe and making connection complete at both ends. (15mtr each.) |  | 1 | Mtr | 100 |  |  | Excess(+) | 480 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | Work of Cable Laying through Trenchless method with HDPE Pipe in pakka Road from 132KV Primary Sub-Station Sector 115, Noida to Medanta Noida, F-16. Sector 50, Noida. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
26 | Fabrication and Errection of Sectional Double Pole Riser by ST Pole 11Mtr. Long for 33KV Line with proper grouting and concreting of pole and proper installation of required accessories as per RESPO norms with complete work in all respect. (all work in the scope of Contractor) Grouting of - In ratio of 1:4:8 in Cement, sand and Brick Ballast) in size 450mmx450mmx1800 mm and Construction of Plinth in size 450x450x300 mm of each (0.285 Cum) pole above the ground level (In ratio of 1:3:6 in Cement, sand and Brick Ballast) as per RESPO. |  | 1 | Job | 100 |  |  | Excess(+) | 16 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | Drilling of dia 220 mm in bores for Single Curcuit by trenchless method by horizontal boring machine at a depth of 1.50 mtrs to 2.50 mtrs. (as per site requirement) below the ground level at Kaccha/Pakka Road/Road Crossing/as per site requirement with complete work in all respect as per RESPO. |  | 1 | Mtr | 100 |  |  | Excess(+) | 5520 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
28 | Laying and interconnecting of above HDPE Pipe PE-80, PN-6, DN-160mm, 6" dia by HDD trenchless method for HOSTING OF 33 KV 3x300sq.mm XLPE cable with complete work in all respect. |  | 1 | Mtr | 100 |  |  | Excess(+) | 5520 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
29 | Laying, Hosting and commissiong of 33 KV 3x300sqmm XLPE Cable Single Ckt. Cable in HDPE Pipe in HDD trenchless method with complete work in all respect. |  | 1 | Mtr | 100 |  |  | Excess(+) | 5520 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
30 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop and making risers at double pole and re-filling of pits in proper manner with required material at kacha/pakka and hot mix road. (All Work and material in the scope of contractor) |  | 1 | Nos. | 100 |  |  | Excess(+) | 16 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
31 | Laying of 33KV 3x300 Sq.mm XLPE Cable in the air on cable Riser Double Pole, existing trench cable trench, G.I.Pipe and making connection complete at both ends. (15mtr each.) |  | 1 | Mtr | 100 |  |  | Excess(+) | 384 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
32 | Preparation, Making and Fixing of 33 KV Power Cable ends: Fixing and Making of 33 KV XLPE Heat shrinkable outdoor jointing kits suitable for 3x300sqmm XLPE Cable after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs with complete connention in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 71 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
33 | Preparation, Making and Fixing of 33 KV Power Cable ends: Fixing and Making of 33 KV XLPE Heat shrinkable Indoor jointing kits suitable for 3x300sqmm XLPE Cable after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs with complete connention in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
34 | Preparation, Making and Fixing of 33 KV Power Cable ends: Fixing and Making of 33 KV XLPE Heat shrinkable Striaght Through Box suitable for 3x300sqmm XLPE Cable after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs with complete connention in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
35 | Laying, Sagging, Re-Sagging of ACSR Dog Conductor as per site requirement with complete work in all respect as per RESPO. |  | 1 | Mtr | 100 |  |  | Excess(+) | 500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
36 | Fixing of 33KV Pin Insulator with Pin as per site requirement with complete work in all respect as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 216 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
37 | Fixing and Driving of MS earth rod of size 20x2500 mm in earth and jointing through G.I. wire of 6 SWG between support and earth electrode by providing proper size of bolts and nuts for pole earthing. |  | 1 | Job | 100 |  |  | Excess(+) | 72 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
38 | Fixing of MS Top Channel 125x65x3200mm as per site requirement with complete work in all respect as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 36 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
39 | Fixing of MS Dropper channel 100x50x2600mm as per site requirement with complete work in all respect as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 108 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
40 | Providing and Wrapping of barbed wire (2.0Kg per Pole) on 33KV ST Poles as anti-climbing device for a length of 0.9Mtr. Wire pitch/gap 13mm and fixing upper and lower end keeping lower end at a height of 2.75Mtr. from the ground, complete with providing and fixing of lower end & upper end clamps made of G.I.Flat 40x5mm complete with nuts&bolts. |  | 1 | Nos. | 100 |  |  | Excess(+) | 72 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
41 | Installation, Commissiong and Fixing of Full Metering System (05 Nos. 3Phase 4 WireStatic TVM, 01 No AMR, 01 No. 33KV Pilfer Proof Metering Cubicle 400/1A) for 33KV Connection and equipments/items related to work and 04No. 33KV CT/PT Double Pole Unit Combine Unit 400/1Amp. mouting at double Pole after fabrication of double pole with proper grouting and concreting at site as per RESPO with complete connections and work in all respect. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
42 | Providing of Aluminium Paint (Company - Berger/Asian/Nerolac/Indigo) and painting the 72Nos. ST 11mtr. Long pole as per RESPO. (All material and work in the scope of contractor) |  | 1 | Ltr | 100 |  |  | Excess(+) | 36 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
43 | Draw making of Cable at Yellow Base for 36 Double Pole riser with complete work in all respect (All work in the scope of Contractor) |  | 1 | Nos. | 100 |  |  | Excess(+) | 36 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
44 | Supply & fixing of Best quality ISI Marked GI Pipe 6" dia for 36 Nos. pole riser suitable for 3x300sqm 33KV cable with complete work in all respect as per RESPO. |  | 1 | Mtr | 100 |  |  | Excess(+) | 432 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
45 | Providing and Fixing of Best Quality Aluminium Binding Wire with complete work in all respect. |  | 1 | Kg. | 100 |  |  | Excess(+) | 18 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
46 | Providing and Fixing of Best Quality Stone Pad300x300x75mm with complete work in all respect. |  | 1 | No. | 100 |  |  | Excess(+) | 72 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
47 | Providing and Fixing of Best Quality MS Nut, Bolt and Washers with complete work in all respect. |  | 1 | Kg. | 100 |  |  | Excess(+) | 126 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
48 | Providing and Fixing of Best Quality MS Clamp with Nut and Bolt and complete work in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 576 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
49 | Providing and Fixing of Best Quality Number Plate with Clamp for Double Pole Risers and complete work in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 36 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
50 | Providing and Fixing of Best Quality Danger Board with clamp for Double Pole Risers and complete work in all respect. |  | 1 | Nos | 100 |  |  | Excess(+) | 36 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
51 | Providing and Fixing of Stone Route Marker in Yellow Colour at the above of 33KV Line for safety purpuse with mentioned PVVNL Property 33KV Line and contact number of concerend JE/SDO/EE and complete work in all respect. (All work in the scope of Contractor.) |  | 1 | Nos. | 100 |  |  | Excess(+) | 40 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
52 | Providing and Fixing of Best Quality Hot Dip Galvanized Earthing of size 1.5"dia with complete work in all respect as per RESPO. (All work in the scope of Contractor) |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
53 | Providing and Fixing of Best Quality Hot Dip Galvanized Earthing Strip of standard size with complete work in all respect as per RESPO. (All work in the scope of Contractor) |  | 1 | Nos. | 100 |  |  | Excess(+) | 40 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
54 | Providing and Fixing of Best Quality 6" Dia RCC Half Round Muffs for HT Cable with complete work in all respect as per RESPO. (All work in the scope of Contractor) |  | 1 | Nos. | 100 |  |  | Excess(+) | 2300 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
55 | SUPPLY AND INSTALLATION OF 33KV RMU AS PER FOLLOWING ; | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
56 | SUPPLY, INSTALLATION AND PROPER COMMISSIONING OF 33KV, 630 Amps. & extensible, outdoor duty (02In- 1Out) fully motorised and manually operated Ring main unit (2 LBS+1VCB/SF6) consisting of copper busbar in SF6/AIR insulated. RMU should be type tested for internal arc of 25 KA for 1 Sec. for Gas tank, Ingress protection (outdoor) IP54 and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel. Suitable CT with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot for termination Kits Or similar technology. Hermitically sealed stainless steel switching chamber. All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibale easy integration with SCADA networks. (Supply of FRTU is not in scope) Aux. PT, Battery, Charger etc. for Motorised operation by remote control. Circuit Breaker protection using a wide range of self-powered and auxiliary relays. Accessible cable Earth & Test Facility at the front of the unit. The scope is including Plinth and Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories. ( Makes: ABB / Siemens / Eaton / Schneider/Lucy/any other make approved in UPPCL) FOR CONSUMER END with complete connections in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
57 | SUPPLY, INSTALLATION AND PROPER COMMISSIONING OF 33KV, 630 Amps. & extensible, outdoor duty (01In - 1Out)fully motorised and manually operated Ring main unit (1 LBS+1VCB/SF6) consisting of copper busbar in SF6/AIR insulated. RMU should be type tested for internal arc of 25 KA for 1 Sec. for Gas tank, Ingress protection (outdoor) IP54 and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel. Suitable CT with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot for termination Kits Or similar technology. Hermitically sealed stainless steel switching chamber. All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibale easy integration with SCADA networks. (Supply of FRTU is not in scope) Aux. PT, Battery, Charger etc. for Motorised operation by remote control. Circuit Breaker protection using a wide range of self-powered and auxiliary relays. Accessible cable Earth & Test Facility at the front of the unit. The scope is including Plinth and Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories. ( Makes: ABB / Siemens / Eaton / Schneider/Lucy/any other make approved in UPPCL) FOR TRANSMISSION END (Sector 115 and 123 Noida) with complete connections in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
58 | Construction of Plinth of size 6'x3'x3' (LxWxH) for above RMUs at site with complete work in all respect. |  | 1 | Job | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
59 | PROVIDING AND INSTALLATION OF CHEMICAL EARTHING FOR ABOVE RMUs (WITH ALL MATERIAL AND LABOUR) AFTER INSTALLATION RESISTANCE SHOULD BE LESS THAN ONE OHM. AS PER FOLLOWING (The all material and labour shall be provided by the contractor with 12 month guarantee for resistance value less than one OHM.) | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
60 | Providing of earth elctrode for chemical earthing Pipe in pipe type proper hot deep galvanization dia 50 mm length 3 mtr - 32mm x 6mm terminal connection hole dia 8mm The cavity between the pipe & pipe is filled with conductive mixture - for hermetically filling inside the cavity i.e. between secondary conductor & primary conductor, crystalline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc the electrode should be sealed from both the ends. The outer pipe of the elctrode should be galavanized the characteristics of this compound is highly cnductive, non magnetic & non corrosive in G.I. Including providing of backfill compound each elctrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested for RMUsF installed at site. |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
61 | Providing and fixing of GI strip of size 32 mm x 6 mm suitable for RMUs installed at Above 33/11 KV Substation . |  | 1 | Mtr | 100 |  |  | Excess(+) | 15 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
62 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. |  | 1 | Mtr | 100 |  |  | Excess(+) | 15 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
63 | FIXING AND CONNECTION OF ABOVE RMU BY 33KV HT 3X300SQMM CABLE AS PER SITE REQUIREMENT WITH COMPLETE CONNECTIONS IN ALL RESPECT. |  | 1 | Mtr | 100 |  |  | Excess(+) | 216 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information