## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle, Hapur.
Name of Work: FOR CONSTRUCTION OF NEW ADDITIONAL DOUBLE POLE AND INCREASING CAPACITY OF TRANSFORMERS AND OHTHER ASSOCIATED WORKS, IN BUSINESS PLAN (2024-25), IN THE AREA OF EDD-I HAPUR, UNDER EDC., HAPUR.
Tender No: 144(W)/EDCH/2023-24
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Increasing Capacity of 100 to 250KVA at various places as per sanctioned estimate, in area of EDD-I Hapur (Third party inspection of the quality of all works will be conducted by the department.) | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Carriage of all petty material of estimate from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001113 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Carriage of all cable/conductor of estimate from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 324 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | Safely dismantling of old 100KVA Transformer from Double Pole after open the connection, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 2 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.04 | Carriage of New 250KVA transformer from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading safely at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 2 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | Construction of T/F plinth suitable for 250KVA T/F (size of 2 x 2 x 1.5 mt.) as per drawing, cc work in foundation in ratio 1:4:8 (Cement, Sand & Brick ballast). Ist class brick work in side walls cc ratio of 1:4 (cement & fine sand). 12mm thick plaster in ratio 1:4 (cement & fine sand). The RCC work on top of plinth in ratio 1:2:4 after duly filling of brick ballast inside the plinth & ramming the same, including cost of all material & labour, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 2 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.06 | Safely installing the New 250KVA transformer with the help of crane/manual labour at LT Sub-Station Double Pole/Plinth, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 2 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.07 | Laying of LT Aluminum XLPE Cable 1x240Sqmm., by providing & fixing of required good quality lugs and completion of work properly as per RESPO/Norms, and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 124 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.08 | Laying of ABC Cable 3x120+1x95+1x16Sqmm., and completion of work properly as per RESPO/Norms, and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 120 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.09 | Connecting of the Jumper of LT & HT side and line energisation work properly, including fixing all required accessories at Double Pole/Plinth, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 2 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.1 | Erection & Fixing of Three Pahse Distribution Box on pole by provding 02 Nos. D/B Clamps & all fixing material, proper size nut & bolts, as per RESPO Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 3 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | Providing and fixing of Suspension Clamp with Eye Hook as per RESPO/Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 12 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | Providing and fixing of L.T. Piercing insulating Clamp as per RESPO/Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 12 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | Providing and fixing of Dead End Clamp with Eye Hook, as per RESPO/Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | Construction of safety fencing (MS) for Transformer 11/0.4 KV Sub Station, With supply of material required for MS fencing (50X50X3 MM) M.S. wire mesh construction utilizing vertical post duly grouted/fitted in ground/on floor. Horizontal angle/T-iron to be fitted on vertical posts. Pickets (if required) fitted to rail and gate to facilitate entry and exit. The vertical Posts/Horizontal post shall be made of M.S. angle 75x75x6mm. Such post shall be kept preferably at distance of 800-1000 MM. and shall be grounded with CC ratio 1:4:8. The length of vertical post shall be sufficient to take care of fencing as requirement at site, and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | Providing and installation of maintenance free multifaceted proactive and corrosion free chemical earthing electrod size 80mm x 3000mm complete with 50KG backfill compound with all required accessories for Body/neutral earthing of Transformers, including cost of M.S. earth strip for connection the earth strip will be welded to the earthing and neutral support, as per RESPO/Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | Carriage of old 100KVA transformer from site of work to JE Store/CTR/ESC, Hapur, with loading & unloading safely at both ends., as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2 | Construction of New 63/100/ 250KVA 11KV Sub-Station Double pole in area of EDD-I Hapur, as per sanctioned estimate. Third party inspection of the quality of all works will be conducted by the department. | BI01010001010000000000000515BI0100001115
2.01 | Carriage of line material (all petty material of estimate) from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.02 | Carriage of all cable/conductor of estimate from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 3944 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.03 | Carriage of ST Pole 11 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 23 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.04 | Carriage of PCC Pole 8.5 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 28 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.05 | Carriage of New 63KVA transformer from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading safely at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.06 | Carriage of New 100KVA transformer from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading safely at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.07 | Carriage of New 250KVA transformer from JE Store/CTR/ESC, Hapur to site of work, including loading & unloading safely at both ends, as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 9 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.08 | Erection of double pole structure with all accessories on ST Pole 11 mtr. long, fabrication and fixing of M.S. Top & Dropper Channel, M.S. T/F Angle, E-Bracket, 11 KV Pin insulator with Pin, Disc Insulator with Disc fitting etc., as per RESPO Drawing/Norms by providing all clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts, and jumpering etc work, and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 8 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.09 | Erection of double pole structure with all accessories on PCC Pole 8.5 mtr. long, fabrication and fixing of M.S. Top & Dropper Channel, M.S. T/F Angle, E-Bracket, 11 KV Pin insulator with Pin, Disc Insulator with Disc fitting etc., as per RESPO Drawing/Norms by providing all clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts, and jumpering etc work, and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 3 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.1 | Erection & Fixing of STP Pole 11 mtr. long in 11 KV line after digging of suitable pits including fixing of requisite all accessories as per RESPO Drawing/Norms by providing F-Bracket and holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts., and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 7 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.11 | Erection & Fixing of PCC Pole 8.5 mtr. long in 11 KV line after digging of suitable pits including fixing of requisite all accessories as per RESPO Drawing/Norms by providing F-Bracket and holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts., and as per direction of site incharge. |  | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.12 | Erection & Fixing of PCC Pole 8.5 mtr. long in LT. line after digging of suitable pits including fixing of requisite all accessories as per RESPO Drawing/Norms by providing L.T. Pin Clamps, M.S. Flat of size 50x6 & Schacle Insulator of size 75x90mm, with proper size nuts and bolts., and as per direction of site incharge. |  | 18 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.13 | Construction of T/F plinth suitable for 250KVA T/F (size of 2 x 2 x 1.5 mt.) as per drawing, cc work in foundation in ratio 1:4:8 (Cement, Sand & Brick ballast). Ist class brick work in side walls cc ratio of 1:4 (cement & fine sand). 12mm thick plaster in ratio 1:4 (cement & fine sand). The RCC work on top of plinth in ratio 1:2:4 after duly filling of brick ballast inside the plinth & ramming the same, including cost of all material & labour and as per direction of site incharge. |  | 9 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.14 | Construction of safety fencing (MS) for Transformer 11/0.4 KV Sub Station, With supply of material required for MS fencing (50X50X3 MM) M.S. wire mesh construction utilizing vertical post duly grouted/fitted in ground/on floor. Horizontal angle/T-iron to be fitted on vertical posts. Pickets (if required) fitted to rail and gate to facilitate entry and exit. The vertical Posts/Horizontal post shall be made of M.S. angle 75x75x6mm. Such post shall be kept preferably at distance of 800-1000 MM. and shall be grounded with CC ratio 1:4:8. The length of vertical post shall be sufficient to take care of fencing as requirement at site, and as per direction of site incharge. |  | 9 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.15 | Providing and installation of maintenance free multifaceted proactive and corrosion free chemical earthing electrod size 80mm x 3000mm complete with 50KG backfill compound with all required accessories for Body/neutral earthing of Transformers, including cost of M.S. earth strip for connection the earth strip will be welded to the earthing and neutral support, as per RESPO/Norms and as per direction of site incharge. |  | 18 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.16 | Safely installing the New 250KVA transformer with the help of crane/manual labour at LT Sub-Station Double Pole/Plinth, as per direction of site incharge. |  | 9 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.17 | Laying of LT Aluminum XLPE Cable 1x240Sqmm., by providing & fixing of required good quality lugs and completion of work properly as per RESPO/Norms, and as per direction of site incharge. |  | 40 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.18 | Laying of LT Aluminum XLPE Cable 1x400Sqmm., by providing & fixing of required good quality lugs and completion of work properly as per RESPO/Norms, and as per direction of site incharge. |  | 324 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.19 | Laying of ABC Cable 3x120+1x95 +1x16Sqmm., and completion of work properly as per RESPO/Norms, and as per direction of site incharge. |  | 805 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.2 | Laying of ABC Cable 3x95+1x70+1x16Sqmm., and completion of work properly as per RESPO/Norms, and as per direction of site incharge. |  | 1020 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.21 | Laying of 11KV HT Cable 3x70Sqmm., overhead line and completion of work properly as per RESPO/Norms, and as per direction of site incharge. |  | 690 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.22 | Laying , Stringing and final sagging of ACSR weasel Conductor, as per RESPO/Drawing Norms and as per direction of site incharge. |  | 1065 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.23 | Connecting of the Jumper of LT & HT side and line energisation work properly, including fixing all required accessories at Double Pole/Plinth, and as per direction of site incharge. |  | 9 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.24 | Installation of 63/100KVA T/F on double pole and line energisation work properly, as per RESPO Norms, and as per direction of site incharge. |  | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.25 | Erection & Fixing of Three Pahse Distribution Box on pole by provding 02 Nos. D/B Clamps & all fixing material, proper size nut & bolts, as per RESPO Norms and as per direction of site incharge. |  | 16 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.26 | Providing and fixing of Suspension Clamp with Eye Hook as per RESPO/Norms and as per direction of site incharge. |  | 13 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.27 | Providing and fixing of L.T. Piercing insulating Clamp as per RESPO/Norms and as per direction of site incharge. |  | 36 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.28 | Providing and fixing of Dead End Clamp with Eye Hook, as per RESPO/Norms and as per direction of site incharge. |  | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.29 | Providing & fixing of Copper L- Pieces 62x225x12mm as per RESPO/Norms and as per direction of site incharge. |  | 4 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.3 | Installation/Erection of 4-Core L.T. MCB with Box, including providing of the same and Completion of properly work as per RESPO Norms and as per direction of site incharge. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.31 | Providing and installation of L.T. ACB with Box, including providing of the same and Completion of properly work as per RESPO Norms and as per direction of site incharge. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.32 | Providing and installation of L.T. Incoming Pannel with Metering MCB Box, including providing of the same and Completion of properly work as per RESPO Norms and as per direction of site incharge. |  | 3 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.33 | Making and filling of 11KV Cable Jointing Kit, 3x70sqmm. Outdoor type, after duly plumbing and taping of suitable XLPE Cable, providing, fixing and crimping of proper size good quality lugs, including cost of lugs and tape etc., as per RESPO Norms and as per direction of site incharge |  | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.34 | Erection & Fixing of 11KV. DO Fuse set on STP/PCC Pole, by providing all required fixing materials as per RESPO/Norms and as per direction of site incharge. |  | 7 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.35 | Erection and Fixing of 11KV Lightening Arrestor by providing all fixing materials and completion work properly as per RESPO Drawing/Norms and as per direction of site incharge. |  | 3 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.36 | Grouting & fixing of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:4:8 cement, sand, 40mm brick ballast as per drg. Including back filling, proper ramming etc and fixing tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing as per RESPO Drawing/Norms by providing all grouting material and stay clamp made of M.S. Flat of size 50x6mm with proper size bolts & nuts & loops., and as per direction of site incharge. |  | 19 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.37 | Earthing of supports with MS earth Rod of (20x2500)mm long including excavation of pit and driving M.S. Rod 3.0 M apart from support and 0.5m below the ground level and connection below the earth electrodes with the help of G.I. wire & earthing lugs as per RESPO Drawing/Norms by providing proper size nuts & bolts., and as per direction of site incharge. |  | 27 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.38 | Grouting of ST/PCC supports in CC 1:4:8 (Cement, sand & 40mm brick ballast) Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, up to ground level, 300mm plinth above the ground level with CC 1:3:6 (Cement, core sand and Stone grit) with mufting as per drawing, work includes back filling & proper ramming by providing all required grouting materials., and as per direction of site incharge. |  | 51 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
2.39 | Jumpering and line energisation work properly as per RESPO/Norms. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information