## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle-I Muzaffarnagar
Name of Work: Under the work area of Executive Engineer, Electricity Distribution Division-I, Muzaffarnagar Subordinate Subdivision Officer, Electricity Distribution Subdivision-III, Muzaffarnagar under the Additional Business Plan 2024-25, Installation of 02 RMUs to eliminate the problem of power disruption of 04 nos. 11 kV industrial feeders emanating from 33/11 KV substation MAKHIYALI, the work of construction should be done through external agency.
Contract No: 48/2024-25/EDC-I/MZN
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only)
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Excluding GST | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 5 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 6 | 54 | 7
1 | The work of delivering following material from the Departmental store center to the site in which includes loading and unloading on both sides. (distance 0 to 50 km) | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | 11 KV XLPE CABLE 3x185 Sqmm |  | 250 | Mtr. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.02 | 11 KV CABLE OUTDOOR JOINTING KIT 3x185 Sqmm |  | 12 | No | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.03 | 11 KV CABLE INDOOR JOINTING KIT 3x185 Sqmm |  | 12 | No | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2 | Complete work of installing the electrical material ( Centralized / Decentralized) at the site. | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.01 | Supply, Installation, testing and commisioning of 11KV RMU 3 Way 12kv 630 Amps 21KA for 3 Sec. SF6 , BIL 28 KV/75 KV peak, push/plug type side extension provision, outdoor, manual operated Ring Mains Unit comprising of 2 load break switch and 1 vaccum circuit breaker (O/G) consisting of busbar in SF6 insulated 304 grade SS tank minimum 2mm thick having type tested reports accordingly. RMU should be front accessible and manufactured in OEM facotry only. Manufacturing through/at authorised partner/integrator shall not be acceptable. RMU should be Type Tested for Internal arc of 21 KA for 1 Sec with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel. Suitable Ct ratio of 300-50/1A, 10P10 2.5VA with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided in case of VCB Feeder with right angle boot for termination Kits, (The scope is including Plinth/ Angle iron Stand as per OEM design complete in all respect as per the direction of Engineer incharge. complete in all respect. |  | 2 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.02 | Providing of earth electrode for chemical earthing Pipe in pipe type proper hot dip Galvanization dia 50mm length 3 mtr- 32mmx 6mm terminal connection hole dia8mm. The cavity between the pipe & Pipe is filled with conductive Mixture- for hermetically Filling inside the cavity i.r. between secondary conductor & Primary conductor, crystalline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductivive carbon/ cement and bonding materail elc. The electrode should be sealed from both the ends. The outer pipe of the electrode should be galvanized the characteristics of this compound. Each electrode should be supplied with bags of 25Kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each) CPRI tested for RMUs installed at above 33/11 KV substations MAKHIYALI. All necessary decentralized materails will be provided by the contractor/Firm. |  | 2 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.03 | Complete work of Laying/ Installation of 11KV XLPE Cable 3x185Sqmm at 33/11KV Sub-station MAKHIYALI as per RESPO standard. In which necessary Decentralized materail will be provided by the contractor/Firm. |  | 250 | Mtr. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.04 | Complete work of Installation and Commissioning of of 11KV XLPE Cable 3x185Sqmm Cable Jointing Kit Indoor at 33/11KV Sub-station MAKHIYALI as per RESPO standard. In which necessary Decentralized materail will be provided by the contractor/Firm. |  | 12 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.05 | Complete work of Installation and Commissioning of of 11KV XLPE Cable 3x185Sqmm Cable Jointing Kit Outdoor at 33/11KV Sub-station MAKHIYALI as per RESPO standard. In which necessary Decentralized materail will be provided by the contractor/Firm. |  | 12 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.06 | Complete work of Fencing of Established RMU at 33/11KV Sub-station MAKHIYALI as per RESPO standard. All necessary Decentralized materail will be provided by the contractor/Firm. |  | 2 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information