## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-II, Noida
Name of Work : fo¦qr forj.k [k.M & xzsVj uks,Mk ds {ks= esa iw.kZ tek ;kstuk ds vUrxZr m¦ku foHkkx ;SMk }kjk lykjiqj v.Mjikl esa fodflr ulZjh gsrq 10 fd0ok0 la;kstu fuxZr djus ds fy, u;h 11 dsoh Hkwfexr ykbZu dk fuekZ.k dk;ZA
Contract No: SHORT TERM E-TENDER NO 127/EUDC-II NOIDA/2023-24
G.S.T. AND ALL TAXES INCLUSIVE IN ALL QUOATED RATES.
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) (Note:- Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC.) The rate quoted by the tenderer shall be inclusive of all duties, taxes (except GST), fees, octroi and other levies, materials, any type of NOC, labour to & FOR transportation of material and labour charges etc. GST AND ALL TAXES INCLUSIVE IN QUOTED RATES. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE per unit In Figures To be entered by the Bidder INCLUSIVE OF ALL TAXES AND GST Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT with All Taxes and GST in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | fo¦qr forj.k [k.M & xzsVj uks,Mk ds {ks= esa iw.kZ tek ;kstuk ds vUrxZr m¦ku foHkkx ;SMk }kjk lykjiqj v.Mjikl esa fodflr ulZjh gsrq 10 fd0ok0 la;kstu fuxZr djus ds fy, u;h 11 dsoh Hkwfexr ykbZu dk fuekZ.k dk;ZA | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Safe carriage of following Centralised/stock material, from any of the Store Center of PVVNL to work site including Loading from Store and safe unloading at site for Item No. 3 to 8 | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | 25 KVA T/F 11/0.4KV |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | ST Pole 11 Mtr. Long |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | 11KV XLPE Cable 3x70sqmm |  | 1 | Mtr. | 100 |  |  | Excess(+) | 240 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | 11KV O/D Termination Kit suitable for 3x70sqmm Cable. |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | ACSR Weasel Conductor |  | 1 | Mtr. | 100 |  |  | Excess(+) | 30 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | Line Accessories ( 11KV Top, Dropper & T- Channel (100x50x2240mm) - 66 Kg., S/S Base Angle for T/F (75x75x6x2240mm) - 30Kg., 11KV Pin Insulator with Pin - 6 Nos., etc.) or any other material releated to work etc.) |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | Supply and Errection of below Following material and Errection of above centralised material for completing the work as per RESPO.
10 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 65x8mm, G.I.Nut bolt & washer, P.G.Clamp, Stone Pad, Al. Binding wire, 'E' bracket 75x10mm, and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as any fabrication work if required & fixing of cross bracing sets 4.3mtr long, from G.I.Angle 65x65x6mm. The work includes cutting holes and providing G.I.Bolt of 16x40mm size, in the middle of the cross bracing with 01No. spring washer of proper size as per drawing/ as per schedule. Double Pole Structures (a) ST - 11 Mtr. Long Pole. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | Grouting of supports in CC 1:3:6 (Cement, sand & 20mm stone grift). Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, upto ground level, 300mm plinth above the ground level with C.C. 1:3:6 (Cement, Course sand and Stone grift) with muffing as per RESPO. Work includes back filling and proper ramming. Double Pole (a) 11M Long STP. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | Installation and Commissioning of 11/0.4 KV, 25 KVA T/F Mounted on Plinth/ Double Pole/Chair as per site requirement and providing & fixing of Lugs & copper L-piece (04 No.) of size 400x50x6mm and making of L.T.Connections with complete work in all respects. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | Fixing and laying of ACSR Weasel conductor for Jumpering as per site requirement. |  | 1 | Mtr | 100 |  |  | Excess(+) | 30 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | FIXING OF PIN INSULATOR WITH PIN AS PER SITE REQUIREMENT. |  | 1 | No. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | FIXING OF MS DROPPER, Top and T- CHANNEL AS PER SITE REQUIREMENT. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | Preparation of 11 KV Power Cable ends: Making of 11 KV XLPE Heat shrinkable outdoor jointing kits suitable for 3x70sqmm XLPE Cable after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs with complete connention in all respect. |  | 1 | No. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | FIXING of Substation Base Angle AS PER SITE REQUIREMENT. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Installation and Fixing of 11 KV Fuse Set: Assembling and installation of fuse set on the fuse set structure of the T/F. The work includes fabrication for proper fixing, if required. Complete work in all respect. |  | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | Providing and Driving of MS earth rod of size 20x2500 mm in earth and jointing through G.I. wire of 6 SWG between support and earth electrode by providing proper size of bolts and nuts for pole earthing. Supply Erection, fixing, grouting of stay rod in cement, sand and brick ballast in ration 1:4:8 in Block 600*600*300 mm with binding & nuzzling including providing & fixing of stay insulator complete in all respect with grouting. (All Work and Material in the scope of Contractor) |  | 1 | No. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | Fixing, tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing, including providing & fixing of Stay Insulators of 11KV and Stay Clamps. |  | 1 | Job | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | Grouting of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:3:6 cement, sand, 20mm Stone grift) as per drg. Including back filling of soil and proper ramming etc. |  | 1 | Job | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | Supply & Laying of HDPE Pipe PE-80, PN-4, DN-140mm dia by HDD trenchless method for 11KV 3x70sq.mm XLPE Double Ckt. cable as per site requirement. (PVVNL GTP APPROVED HDPE PIPE SHALL BE SUPPLIED WITH INSPECTION.) |  | 1 | Mtr | 100 |  |  | Excess(+) | 160 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
23 | Drilling of dia 220 mm in two parallel bores for Double Curcuit by trenchless method by horizontal boring machine at a depth of 1.50 mtrs to 2.50 mtrs. (as requirement at site) below the ground level in hot mixed road with complete work in all respect as per RESPO. |  | 1 | Mtr | 100 |  |  | Excess(+) | 160 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
24 | Laying of 11KV Double Ckt. 3x70Sq.mm XLPE cable in HDPE Pipe. |  | 1 | Mtr | 100 |  |  | Excess(+) | 160 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop FOR making risers at double pole and re-filling of pits in proper manner with required material at kacha/pakka and hot mix road. (All Work and material in the scope of contractor) |  | 1 | Job | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
26 | Laying of 11 KV 3X70 Sq.mm XLPE Cable in the air on cable Riser Double Pole, existing trench cable trench, nala x-ing & Providing 24 Mtr. GI Pipe 6" Inch Dia and making connection with 11KV over head line at both ends. |  | 1 | Mtr | 100 |  |  | Excess(+) | 80 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | Providing and Fixing of MS Holding Clamps as per site requirement. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
28 | Providing and Fixing of MS Nut, Bolt and Washers as per site requirement. |  | 1 | Kg | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information