## BoQ1 (hidden)
Item Wise BoQ
BoQ_Ver3.0 | Item Wise | Normal | INR Only | INR
Select, Excess (+), Less (-)
Tender Inviting Authority: Executive Engineer, Electricity Construction & Works Division, Ghaziabad | [54 empty] | Bought Out
Name of Work:-Works at proposed Construction of 33KV line for feeding 33/11KV Substation Jewar Air Port (Jewar) from Sec-18, YEIDA Substation Jewar Greater Noida. | [54 empty] | Direct
Tender Reference No : 72/ECWD/Gzb/2023-24 | [54 empty] | Quote for Supply Portion only
Bidder Name : | [54 empty] | Quote for Erection Portion only
PRICE BID 1. This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns after validating the sheet, else the bidder is liable to be rejected for this tender. 2. Bidders are allowed to enter the Bidder Name and Unit Ex-Works Price and GST in %age only. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents. 9. BIDDERS MUST FILLED UP THE GST IN %AGE OTHERWISE G.S.T. RATES WILL BE TREATED AS INCLUDED IN THE GIVEN BASIC RATES.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Description of Works | Item Code | Tendered Quantity | Unit | Estimated Rate | Bought-out /Direct | Specify Bought-out /Direct | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Ex-Works Price (Rs./Unit) | Excise Duty (Rs/Unit) | CST/VAT (Rs/Unit) | Other Taxes & Duties (Rs/Unit) | Freight & Insurance Charges (in Rs./Unit) |  |  | Unit FOR Dest. Supply Price incl. all Taxes and Duties (in Rs./Unit) (F+G+H+I+J) | Total Value for work (In Rs.) (C x F) | GST (in %age) | Total Value for GST (in Rs.) |  |  | Total Unit Price incl. GST (in Rs.) | [26 empty] | Total Amount excl. GST (in Rs.) | Total Amount incl. GST (in Rs.) | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Supply of following Material Supply of Stay set complete (G.I.Stay rod 20x1800mm, Stay wire 7/8SWG 10Kg, Guy insulator, G.I.Stay clamp 65x8mm size with nuts, bolts & washers with concrete grouting) for 33KV line as per PVVNL approved vendor. | item1 | 352 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [8 empty] | 18 |  | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2 | Supply of G.I. Wire 6 SWG as per PVVNL approved vendor. | item2 | 600 | Kg | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
3 | Supply of G.I. Wire 8 SWG as per PVVNL approved vendor. | item3 | 200 | Kg | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
4 | Supply of G.I. Wire 16 SWG as per PVVNL approved vendor. | item4 | 20 | Kg | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
5 | Supply of V-Type Cross Arm 100x50x6 mm G.I channel for 33KV line with G.I.Clamp 75x10mm size with nuts, bolts & washers as per PVVNL approved vendor. | item5 | 260 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
6 | Supply of G.I.Top Channel 125x65x6mm, 3200 mm long (13.10kg/mt) with G.I. clamp of 75x10mm size with nuts, bolts & washers for 33KV line double pole/ Four Pole as per PVVNL approved vendor. | item6 | 51 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
7 | Supply of G.I. Channel 100x50x6 mm, 2400 mm long (9.56kg/mt) with G.I.Clamp of 65x8mm size with nuts, bolts & washers for dropper channel of 33KV line double pole/four pole as per PVVNL approved vendor. | item7 | 71 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
8 | Supply of G.I Angle Iron 65x65x6mm, (5.80kg/mt) 4300 mm long bracing with 4 Nos. G.I. clamps of 65x6mm size with nuts, bolts & washers for 33KV line as per PVVNL approved vendor. | item8 | 32 | Set. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
9 | Supply of G.I Guarding angle 75x75x6 mm, (6.80kg/mt) x 2200mm long with 02 No. G.I.Clamps of 65x8mm size with nuts, bolts & washers. as per PVVNL approved vendor. | item9 | 40 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
10 | Supply of G.I.Cable support Structure (by using of 100x50x6mm channel & its bracing on angle of size 50x50x6mm as per PVVNL approved vendor. | item10 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
11 | Supply of Earthing of Pole by M.S.Earthing Rod 2540x20mm & 6SWG G.I.Earthing wire (2.0Kg) complete in all respects. | item11 | 358 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
12 | Supply of 33KV G.I. "E"-bracket of 75x10mm size with nuts, bolts & washers as per PVVNL approved vendor. | item12 | 156 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
13 | Supply of 33KV G.I. "F"- bracket for STP of 75x10mm size with nuts, bolts & washers as per PVVNL approved vendor. | item13 | 260 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
14 | Carriage of following material from PVVNL store as per availability A.C.S.R. Dog Conductor | item14 | 39969 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
15 | Cable H.T.XLPE 33KV 3x300SQ.M.M | item15 | 21550 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
16 | Steel Tubler Pole SP-55 11.00Mtr | item16 | 310 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
17 | Steel Tubler Pole SP-72 13.00Mtr | item17 | 48 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
18 | 33KV composite Polymeric Pin insulator. | item18 | 936 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
19 | 33KV Polymer Disc insulator B&S 70KN | item19 | 228 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
20 | 33KV Disc fitting B&S Dog/Racoon 70KN | item20 | 228 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
21 | Heat Shrinkable outdoor type end termination cable jointing kit suitable for 33KV XLPE 3x300 Sq. mm.cable | item21 | 50 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
22 | Heat Shrinkable indoor type end termination cable jointing kit suitable for 33KV XLPE 3x300 Sq. mm.cable | item22 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
23 | Heat Shrinkable straight through cable jointing kit suitable for 33KV XLPE 3x300 Sq. mm.cable | item23 | 40 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
24 | Erection of Following Material & Miscellaneous Electrical Works. Fabrication and erection of cable support made of two pieces of G.I.Channel (100x50x6)mm, 2.75 meter long, joined to each other by means of 02 Nos. G.I.Channel (100x50x6)mm & 03 Nos. G.I.Angle (50x50x6) mm pieces of size 1.0Mtr long each by welding at equal intervals and grouting in a block of size (300x1000x1000)mm in C.C. 1:3:6. Work includes providing of three Nos. G.I. clamps made of (50x6)mm G.I. Flat for holding the cable including nuts and bolts with stone Pad of size (300x300x75mm). | item24 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
25 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 'F' bracket 75x10mm, G.I.Nut bolt & washer, Stone Pad Al. Binding wire and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as an fabrication work if required. (a) Single Pole (i) 11M Long STP, SP-55 Round Pole | item25 | 220 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
26 | (ii) 13M Long STP, SP-72 Round Pole | item26 | 40 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
27 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 65x8mm, G.I.Nut bolt & washer, P.G.Clamp, Stone Pad, Al. Binding wire, 'E' bracket 75x10mm, and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as any fabrication work if required & fixing of cross bracing sets 4.3mtr long, from G.I.Angle 65x65x6mm. The work includes cutting holes and providing G.I.Bolt of 16x40mm size, in the middle of the cross bracing with 01No. spring washer of proper size as per drawing/ as per schedule. (a) Double Pole Structures (i) 11M Long STP, SP-55 Round Pole | item27 | 26 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
28 | (ii) 13M Long STP, SP-72 Round Pole | item28 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
29 | (b) End Double Pole Structures (i) 11M Long STP, SP-55 Round Pole | item29 | 12 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
30 | (c) Four Pole Structures (i) 11M Long STP, SP-55 Round Pole | item30 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
31 | Riser Double Pole The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all clamps size (65x8mm), Nut bolt & Washer, Stone Pad, Lugs, Al. Binding wire and other accessories as per drawing. The work includes carriage and handling of supports & hardware material from sectional store to pit site as well as an fabrication work if required. Fixing of 04 Nos. G.I.Channel 100x50x2.4Mtr (With arrangement of 06 Nos. 33KV Pin insulator with Pin). The work also includes cutting of channel/angles, making holes on G.I.Channel / G.I. Angle, spring washer of proper size for channel/angle. Contractor also provide G.I.Channel clamps and E- clamps at his own cost as per Respo Norms. (a) 11M Long STP, SP-55 Round Pole | item31 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
32 | Grouting of supports in CC 1:3:6 (Cement, sand & 20mm stone grift). Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, upto ground level, 300mm plinth above the ground level with C.C. 1:3:6 (Cement, Course sand and Stone grift) with muffing as per drawing. Work includes back filling and proper ramming. (a) Single Pole (i) 11M Long STP, SP-55 Round Pole | item32 | 220 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
33 | (ii) 13M Long STP, SP-72 Round Pole | item33 | 40 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
34 | (b) Double Pole Structures (i) 11M Long STP, SP-55 Round Pole | item34 | 26 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
35 | (ii) 13M Long STP, SP-72 Round Pole | item35 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
36 | (c) End Double Pole Structures (i) 11M Long STP, SP-55 Round Pole | item36 | 12 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
37 | (d) Riser Double Pole (i) 11M Long STP, SP-55 Round Pole | item37 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
38 | (c) Four Pole Structures (i) 11M Long STP, SP-55 Round Pole | item38 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
39 | Grouting of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:3:6 cement, sand, 20mm Stone grift) as per drg. Including back filling of soil and proper ramming etc. | item39 | 352 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
40 | Fixing, tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing, including providing & fixing of Stay Insulators of 33KV and Stay Clamps. | item40 | 352 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
41 | Earthing of supports with M.S.Earth Rod of (20x2540)mm long including excavation of pit and driving M.S.Rod 3.0M apart from support and 0.5M below the ground level and connecting below the earth electrodes with the help of G.I.wire No.8SWG, G.I.Nut bolt & washer and earthing lugs. | item41 | 358 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
42 | Laying, spreading, lifting and final sagging of 3 phases ACSR Dog conductor in accordance with Line chart includidng providing binding wire, binding and fixing of all accessories in 03Nos. Conductor in parallel. | item42 | 39969 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
43 | Making Jumpers on Sectional Pole, by providing & fixing of P.G.Clamps of proper sizes, suitable for Dog Conductor/ 33KV, 3x300Sq.mm XLPE cable (12 Nos. P.G.Clamps at each section double Pole & 06 No. P.G.Clamps at each end double Pole (a) Sectional Double Pole | item43 | 30 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
44 | (b) End Double Pole | item44 | 12 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
45 | (c) Riser Double Pole | item45 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
46 | (d) Four Pole Structures | item46 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
47 | Guarding between two poles like single poles, double poles, four poles, etc. to guard L.T., 11KV Line telephone line and river crossing, road crossing etc. with G.I.wire No.6SWG, G.I.wire No.8SWG and G.I.wire No.16SWG including cutting with fabrication and fixing of G.I.Guarding angle 75x75x6mm with Providing & fixing G.I.clamps size 65x8mm, G.I.Turn buckle, G.I.Eye bolt, nut bolts & washer, & bearer wire 04 Nos. etc, as per drawing. | item47 | 20 | Per Span | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
48 | Providing & fixing of SMC Danger board at each Pole as per specification of the drawing. Size 200mmx250mm & 3mm thickness with G.I.Clamp & nut & bolt for 33KV | item48 | 358 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
49 | Providing & fixing of SMC Number Plate at each Pole as per specification of the drawing. Size 200mmx250mm & 3mm thickness with G.I.Clamp & nut & bolt. | item49 | 358 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
50 | Chopping of branches of trees of eucalyptus, Neem, Keekar and other kind of trees along the route of the line and disposal of the same at suitable place. | item50 | 6 | Per Km. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
51 | Providing & Wrapping of barbed wire (2.0Kg per Pole) on 33KV ST Poles SP-55/SP-72 as anti-climbing device for a length of 0.9Mtr. Wire pitch/gap 13mm and fixing upper and lower end keeping lower end at a height of 2.75Mtr. from the ground, complete with providing and fixing of lower end & upper end clamps made of G.I.Flat 40x5mm complete with nuts&bolts. | item51 | 358 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
52 | Painting of following supports/structures of 33KVLine, with two coats of synthetic enamel aluminium paint after one coat of ready mix primer, including cost of all material, as well as rubbing/cleaning of surface as required for proper completion of work:- (a) 11Mtr SP-55 Poles including all channels/x-arms/clamps etc. (i) Single Supports | item52 | 220 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
53 | (ii) Double Pole Structure | item53 | 26 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
54 | (iii) Cable Riser | item54 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
55 | (iv) End Pole | item55 | 12 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
56 | (v) Four Pole | item56 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
57 | (b) 13Mtr SP-72 Poles including all channels/x-arms/clamps etc.: (i) Single Supports | item57 | 40 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
58 | (ii) Double Pole Structure | item58 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
59 | Digging of Trench by excavation of earth of 1300x750mm size for 33KV line | item59 | 9875 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
60 | Safe laying of 33KV, 3x300Sq.mm. XLPE Cable in Cable | item60 | 19750 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
61 | Providing & Laying of Ist Class Bricks, along the length on both side of 33KV XLPE Cable in Cable Trench (minium 18No. Bricks/Mtr) and Stone Slab of size 450x600x40mm on top of the Cable, Providing 150mm thickness River sand for cushion beneath and 150mm above the cable as per specification. | item61 | 9875 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
62 | Back filling of excavated earth in the cable trench upto the ground level and ramming properly. | item62 | 9875 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
63 | Supply & Laying of HDPE Pipe PE-80, PN-6, DN-160mm dia by HDD trenchless method, as per site requirement. | item63 | 1300 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
64 | Laying of 33KV, 3x300Sq.mm XLPE cable in HDPE Pipe PE-80, PN-6, DN-160mm dia by HDD trenchless method, as per site requirement. | item64 | 1300 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
65 | Laying of 33KV, 3x300Sq.mm XLPE Cable in the air on cable Riser Double Pole and nala x-ing & G.I.Pipe making connection with 33KV over head line at both ends. | item65 | 500 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
66 | Providing & Fixing 150mm dia 2mm thick 3M long G.I.Pipe over 33KV, 3x300Sq.mm XLPE Cable before mounting the 2No. Cable on double pole / Cable support structure. The work includes Providing & fixing of Clamp, sealing of top and bottom end of the G.I.Pipe. One end of G.I.Pipe is to be buried under earth about 500mm. | item66 | 50 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
67 | Making of 33KV Outdoor type cable end termination by heat shrinkable XLPE Cable Jointing Kits and crimping with proper size aluminium lugs. Work includes providing Aluminum lugs, insulating tapes etc as per specifications. | item67 | 50 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
68 | Making of 33KV indoor type cable end termination by heat shrinkable XLPE Cable Jointing Kits and crimping with proper size aluminium lugs. Work includes providing Aluminum lugs, insulating tapes etc as per specifications. | item68 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
69 | Making of 33KV Straight through Cable Jointing Kits 3x300mm² and crimping of proper size aluminium lugs. Work includes providing insulating tapes etc as per specifications. | item69 | 40 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
70 | Supply & fixing of cable route marker along the route of 33KV cable with proper grouting with proper painting & marking PVVNL, 33KV HT Cable. | item70 | 50 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
71 | Road restoration charges for 1Mtr wide Kuccha Road (Inter locking Tiles, Bricks Road & Developed green belt only) or Deposite charges to take the permission/approval/NOC from any Development Authority/Govt. Body/Forest Deptt./and other concerned Deptt. for construction of 33KV line | item71 | 100 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
72 | Road restoration charges for 1Mtr wide Pucca Road (Cemented, Concrete & Black road only) or Deposite charges to take the permission/approval/NOC from any Development Authority/Govt. Body/Forest Deptt./and other concerned Deptt. for construction of 33KV line | item72 | 250 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
73 | Cartage of empty cable drum from site to PVVNL store including loading & unloading at both ends respectively. | item73 | 43 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
74 | To provide required No. of technicians to work on 33KV line during testing, commissioning & energisation. | item74 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
75 | 50mm thick RCC work on top of the HDPE Pipe, PE-80, PN-6, DN-160 at road crossing inside of the airport boundry should be done by the Contractor | item75 | 250 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
Total in Figures | [51 empty] | 0 | 0 |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [7 empty] | % | [39 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information