## BoQ1 (hidden)
Item Wise BoQ
BoQ_Ver3.0 | Item Wise | Normal | INR Only | INR
Select, Excess (+), Less (-)
Tender Inviting Authority: Executive Engineer, Electricity Construction & Works Division, Ghaziabad | [54 empty] | Bought Out
Name of Work:-(i) Maintenance of 33KV line Koyal Enclave from 220KV Substation Morti to 33/11KV Substation Koyal Enclave-II from Lajpat nagar Road Oppsite Ex. D/P to Eucalyptus Ex. D/P (ii) Maintenance, Removing Damage Pole of 33KV line for feeding 33/11KV Substation Sidharath Vihar, Ghaziabad from 220KV Substation Rathi Ispath, Ghaziabad. | [54 empty] | Direct
Tender Reference No : 52/ECWD/Gzb/2023-24 | [54 empty] | Quote for Supply Portion only
Bidder Name : | [54 empty] | Quote for Erection Portion only
PRICE BID 1. This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns after validating the sheet, else the bidder is liable to be rejected for this tender. 2. Bidders are allowed to enter the Bidder Name and Unit Ex-Works Price and GST in %age only. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents. 9. BIDDERS MUST FILLED UP THE GST IN %AGE OTHERWISE G.S.T. RATES WILL BE TREATED AS INCLUDED IN THE GIVEN BASIC RATES.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Description of Works | Item Code | Tendered Quantity | Unit | Estimated Rate | Bought-out /Direct | Specify Bought-out /Direct | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Ex-Works Price (Rs./Unit) | Excise Duty (Rs/Unit) | CST/VAT (Rs/Unit) | Other Taxes & Duties (Rs/Unit) | Freight & Insurance Charges (in Rs./Unit) |  |  | Unit FOR Dest. Supply Price incl. all Taxes and Duties (in Rs./Unit) (F+G+H+I+J) | Total Value for work (In Rs.) (C x F) | GST (in %age) | Total Value for GST (in Rs.) |  |  | Total Unit Price incl. GST (in Rs.) | [26 empty] | Total Amount excl. GST (in Rs.) | Total Amount incl. GST (in Rs.) | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Supply of following Material (Sl.No.01 to 03) G.I. Channel 100x50x6 mm, 2400 mm long (9.56kg/mt) with G.I.Clamp of 65x8mm for dropper channel of 33KV line double pole/four pole | item1 | 5 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [8 empty] | 18 |  | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2 | Heat Shrinkable outdoor type end termination cable jointing kit suitable for 33KV XLPE 3x300 Sq. mm.cable | item2 | 16 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
3 | Heat Shrinkable straight through cable jointing kit suitable for 33KV XLPE 3x300 Sq. mm.cable | item3 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
4 | Carriage of following material from PVVNL store (Sl.No.04 to 05) Cable H.T.XLPE 33KV 3x300SQ.M.M | item4 | 2000 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
5 | 33KV composite Polymeric Pin insulator. | item5 | 15 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
6 | Erection of Following Material & Miscellaneous Electrical Works. Making Jumpers on Sectional Pole, by providing & fixing of P.G.Clamps of proper sizes, G.I.Nut bolt & washer etc; suitable for Dog Conductor/ 33KV, 3x300Sq.mm XLPE cable. (i) Existing Riser Double Pole | item6 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
7 | Digging of Trench by excavation of earth of 1050x750mm size for 33KV line | item7 | 80 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
8 | Safe laying of 33KV, 3x300Sq.mm. XLPE Cable in Cable Trench to respective Double Pole. | item8 | 160 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
9 | Providing & Laying of Ist Class Bricks, along the length on both side of 33KV XLPE Cable in Cable Trench (minium 18No. Bricks/Mtr per Cable) and Stone Slab (Smooth surface both side) of size 400x600x40mm on top of the Cable, Providing 150mm thickness River sand for cushion beneath and 150mm above the cable as per specification. | item9 | 80 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
10 | Back filling of excavated earth in the cable trench upto the ground level and ramming properly. | item10 | 80 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
11 | Supply & Laying of HDPE Pipe PE-80, PN-6, DN-160mm dia by HDD trenchless method, as per site requirement. | item11 | 1680 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
12 | Laying of 33KV, 3x300Sq.mm XLPE cable in HDPE Pipe PE-80, PN-6, DN-160mm dia by HDD trenchless method, as per site requirement. | item12 | 1680 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
13 | Laying of 33KV, 3x300Sq.mm XLPE Cable in the air on cable Riser Double Pole, existing cable trench, Pucca trench, nala x-ing & G.I.Pipe and making connection with 33KV over head line at both ends. | item13 | 160 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
14 | Providing & Fixing 150mm dia 2mm thick 3M long G.I.Pipe over 33KV, 3x300Sq.mm XLPE Cable before mounting the 2No. Cable on double pole / Cable support structure. The work includes fixing of Clamp, sealing of top and bottom end of the G.I.Pipe. One end of G.I.Pipe is to be buried under earth about 500mm. | item14 | 16 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
15 | Making of 33KV Outdoor type cable end termination by heat shrinkable XLPE Cable Jointing Kits and crimping with proper size aluminium lugs. Work includes providing Aluminum lugs, insulating tapes etc as per specifications. | item15 | 16 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
16 | Making of 33KV Straight through Cable Jointing Kits 3x300mm² and crimping of proper size aluminium lugs. Work includes providing insulating tapes etc as per specifications. | item16 | 2 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
17 | Supply & fixing of cable route marker along the route of 33KV cable with proper grouted with proper painting & marking PVVNL, 33KV HT Cable. | item17 | 5 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
18 | Fixing of extra Dropper Channels on existing four Pole with providing & fixing of all G.I.Clamps size of 65x8mm, 'F' bracket 75x10mm, G.I.Nut bolt & washer, P.G.Clamps, Al. Binding wire and other accessories & fixing of Pin Insulators, jumpering with P.G.Clamps, clamping and binding etc,as per site conditions. | item18 | 5 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
19 | Climbing, fixing & tightening of extra 33KV composite polymeric Pin insulator on old existing Riser double Pole. | item19 | 15 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
20 | Road restoration charges for 1Mtr wide Kuccha Road (Inter locking Tiles, Bricks Road & Developed green belt only) or Deposite charges to take the permission/approval/NOC from any Development Authority/Govt. Body/Forest Deptt./and other concerned Deptt. for restoration of damaged property like Kuccha road, Inter locking Tiles and other utilities. | item20 | 500 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
21 | Road restoration charges for 1Mtr wide Pucca Road (Cemented, Concrete & Black road only) or Deposite charges to take the permission/approval/NOC from any Development Authority/Govt. Body/Forest Deptt./and other concerned Deptt. for restoration of damaged property like Pucca road, Inter locking Tiles and other utilities. | item21 | 20 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
22 | Cartage of empty cable drum from site to PVVNL store including loading & unloading at both ends respectively. | item22 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
23 | (ii) Maintenance, Removing Damage Pole of 33KV line for feeding 33/11KV Substation Sidharath Vihar, Ghaziabad from 220KV Substation Rathi Ispath, Ghaziabad. Supply of following Material (Sl.No.23 to 26) Stay set complete (G.I.Stay rod 20x1800mm, Stay wire 7/8SWG 10Kg, Guy insulator, G.I.Stay clamp, bolt, nut & wasther with concrete grouting) for 33KV line as per specification | item23 | 8 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
24 | V-Type Cross Arm 100x50x6 mm G.I channel for 33KV line with G.I.Clamp 75x10mm size | item24 | 5 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
25 | G.I.Top Channel 125x65x6mm, 3200 mm long (13.10kg/mt) with G.I. clamp of 75x10mm size, bolts, nuts and washers for 33KV line double pole/ Four Pole | item25 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
26 | G.I Angle Iron 65x65x6mm, (5.80kg/mt) 4300 mm long (02 No.) for bracing set with 4 Nos. G.I. clamps of 65x6mm, bolts, nuts and washers for 33KV line | item26 | 1 | Set. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
27 | Carriage of following material from PVVNL store (Sl.No. 27 to 31) A.C.S.R. Dog Conductor | item27 | 30 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
28 | Steel Tubler Pole SP-55 11.00Mtr | item28 | 7 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
29 | 33KV composite Polymeric Pin insulator. | item29 | 22 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
30 | 33KV Polymer Disc insulator B&S 70KN | item30 | 10 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
31 | 33KV Disc fitting B&S Dog/Racoon 70KN | item31 | 10 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
32 | Erection of Following Material & Miscellaneous Electrical Works. The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support structure, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 'F' bracket 75x10mm, G.I.Nut bolt & washer, Stone Pad Al. Binding wire and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as an fabrication work if required. Single Pole (a) 11M Long STP, SP-55 Round Pole | item32 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
33 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 65x8mm, G.I.Nut bolt & washer, P.G.Clamp, Stone Pad, Al. Binding wire, 'E' bracket 75x10mm, and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as any fabrication work if required & fixing of cross bracing sets 4.3mtr long, from G.I.Angle 65x65x6mm. The work includes cutting holes and providing G.I.Bolt of 16x40mm size, in the middle of the cross bracing with 01No. spring washer of proper size as per drawing/ as per schedule. Double Pole Structures (a) 11M Long STP, SP-55 Round Pole | item33 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
34 | Grouting of supports in CC 1:3:6 (Cement, sand & 20mm stone grift). Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, upto ground level, 300mm plinth above the ground level with C.C. 1:3:6 (Cement, Course sand and Stone grift) with muffing as per drawing. Work includes back filling and proper ramming. Single Pole (a) 11M Long STP, SP-55 Round Pole | item34 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
35 | Double Pole Structures (a) 11M Long STP, SP-55 Round Pole | item35 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
36 | Grouting of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:3:6 cement, sand, 20mm Stone grift) as per drg. Including back filling of soil and proper ramming etc. | item36 | 8 | Set | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
37 | Fixing, tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing, including providing & fixing of Stay Insulators of 33KV and Stay Clamps. | item37 | 8 | Set | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
38 | Providing & Earthing of supports with M.S.Earth Rod of (20x2500)mm long including excavation of pit and driving M.S.Rod 3.0M apart from suppor and 0.5M below the ground level and connecting belowl the earth electrodes with the help of G.I.wire No.6SWG, G.I.Nut bolt & washer and earthing lugs. | item38 | 7 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
39 | Laying, spreading, lifting and final sagging of 3 phases ACSR Dog conductor in accordance with Line chart includidng binding and fixing of all accessories in 03Nos. Conductor in parallel. | item39 | 30 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
40 | Making Jumpers on Sectional Pole, by providing & fixing of P.G.Clamps of proper sizes, suitable for Dog Conductor/ 33KV, 3x300Sq.mm XLPE cable. Sectional Double Pole | item40 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
41 | Providing & fixing of SMC Danger board at each location as per specification of the drawing. Size 200mmx250mm & 3mm thickness with G.I.Clamp & nut & bolt for 33KV | item41 | 6 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
42 | Providing & fixing of SMC Number Plate at each location as per specification of the drawing. Size 200mmx250mm & 3mm thickness with G.I.Clamp & nut & bolt. | item42 | 6 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
43 | Providing & Wrapping of barbed wire (2.0Kg per Pole) on 33KV ST Poles SP-55/SP-72 as anti-climbing device for a length of 0.9Mtr. Wire pitch/gap 13mm and fixing upper and lower end keeping lower end at a height of 2.75Mtr. from the ground, complete with providing and fixing of lower end & upper end clamps made of G.I.Flat 40x5mm complete with nuts&bolts. | item43 | 7 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
44 | Supply of Al. Paint & Red oxide Paint as per IS mark & PVVNL specification & Painting of following supports/structures of 33KVLine, with two coats of synthetic enamel aluminium paint after one coat of ready mix primer, including cost of all material, as well as rubbing/cleaning of surface as required for proper completion of work:- 11Mtr SP-55 Poles including all channels/x-arms/clamps etc (i) Single Supports | item44 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
45 | (ii) Double Pole Structure | item45 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
46 | Climbing, Fixing & tightening of extra of 33KV Composite Polymeric Pin insulator on old existing poles in place of broken & damaged Pin insulator. | item46 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
47 | Climbing, Fixing & tightening of extra 33KV Polymeric Disc insulator B&S 70KN on old existing poles in place of broken & damaged Disc insulator | item47 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
48 | Climbing, Fixing & tightening of extra 33KV Disc fitting B&S 70KN on old existing poles in place of broken & damaged Disc fitting. | item48 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
49 | Removal & Dismantling of damaged ST single Pole from single Ckt 33KV line with all accessories after digging of Pits for taking out of poles & stacking the Pole at proper place & back filling of soil in Pits & proper ramming etc. | item49 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
50 | Removal & Dismantling of damaged ST double Pole from S/Ckt 33KV line with all accessories after digging of Pits for taking out of poles & stacking the Pole at proper place & back filling of soil in Pits & proper ramming etc. | item50 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
51 | Removal & Diamantling of damaged Pin insulator with Pin of 33KV line and stacking the Pin scrap at a proper place in safe position. | item51 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
52 | Removal & Diamantling of damaged Disc insulator of 33KV line. | item52 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
53 | Removal & Diamantling of damaged Disc fitting of 33KV line and stacking the Disc fitting scrap at a proper place in safe position. | item53 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
54 | Safe carriage of old received back material from site to PVVNL store including loading & unloading at both end. | item54 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
Total in Figures | [51 empty] | 0 | 0 |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [7 empty] | % | [39 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information