# GUARANTEED TECHNICAL PARTICULARS  FOR METERING CUBICLE

Tender No. PVVNL-MT/COM/21(s)/22-23

| Sr. No. | Particulars | Required Parameters | Submitted by the Firm |
| --- | --- | --- | --- |
| 1. | Material of the Meter Box | SMC IS : 13410 (THERMOSETTING PLASTIC) Grade S 1 |  |
| 2. | Color of Box | Gray/OFF white |  |
| 3. | Dimension of Box (L X W X H) | 900x350x250mm |  |
| 4. | THICKNESS OF BOX | 2.5mm (Min.) |  |
| 5. | Clearance between meter and meter box between the following: |  |  |
| I | Top | 50 mm (Min.) |  |
| II | Both sides | 50 mm (Min.) |  |
| III | Bottom Meter Surface to partition plate | 50mm(Approx.) |  |
| IV | Front side | 50mm (Min.) |  |
| 6. | No. of Hinges |  |  |
| I | For Meter Compartment Door | SS Strip Concealed Hinge |  |
| II | For CTs Compartment Door | SS Strip Concealed Hinge |  |
| 7. | Viewing Window |  |  |
| I | Material | Toughened Glass |  |
| II | Dimensions | 170x85mm (Min 2 mm thick) |  |
| III | Whether shade arrangement to window provided or not | SMC Flap |  |
| 8(a). | Sealing arrangement | Holes for wire seal |  |
| (b) | Arrangements for Pad-locks | Suitable size holes to be provided in meter chamber as well as C.T. chamber with SS U clamp for pad -locks. |  |
| 9. | Whether sufficient sealing provided to make dust, water and vermin proof? | Rubber Gasket |  |
| 10a. | Whether inlet and outlet arrangement for service cable provided. Please mention dimension of holes? | Side Entry |  |
| b | ## Whether for incoming and outgoing cables provisions of HDPE glands of suitable size have been made. Please mention its dimension? | 8 Nos. PVC Collapsible glands, 4 nos. on each side of CT chamber for CT ratio 50/5 A to 600/5 A 16 Nos. PVC Collapsible glands, 8 nos. on each side of CT chamber for CT ratio 800/5A to 1600/5 A Size of glands for various CTs ratios :- - For CT ratio 50/5A to 400/5A PVC Collapsible Gland 25 mm. - For CT ratio 600/5A PVC Collapsible Gland 35 mm. - For CT ratio 800/5A to 1600/5A PVC Collapsible Gland 50 mm. |  |
| 11. | - Meter Fixing arrangements | Adjustable (SMC Sheet) |  |
|  | - Whether suitable hanging arrangement for meter box firmly on pole is provided? | Yes MS Flat Provided |  |
| 12. | CT Fixing Arrangements | On SMC Mounting plate |  |
| 13. | Earthing Provision | M6x20mm Bolt (Brass) |  |
| 14. | Tests |  |  |
| 14.1 | Water Absorption | ASTMD 570 or IS :14772-2000 Requirement <0.4% |  |
| 14.2 | Mechanical Strength Test | IS: 14772-2000 |  |
| 14.3 | Stability at High Temperature | IS: 14772-2000 |  |
| 14.4 | Material Identification |  |  |
| a) | Presence of Reinforcement | TGA Method and its percentage |  |
| b) | % Reinforcement | IS 13411 |  |
| c) | Exposure to flame | IS 4249 Self extinguishing |  |
| d) | Identification of Polymer | SMC IS 13410 |  |
| 15.0 | Grade of Material | SMC IS: 13410 Grade S-1 |  |
| 15.1 | Properties of material of construction |  |  |
| a) | Heat Deflection Temp. (Ref ISO-75) | 170 deg. Cel. |  |
| b) | Melting point (Test up to 250 dec. cel. (Ref standard IS 13360) | IS: 13360 PART 6 Section Method 'A' Capillary Tube Method. |  |