## BoQ1 (hidden)
Item Wise BoQ
BoQ_Ver3.0 | Item Wise | Normal | INR Only | INR
Select, Excess (+), Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle, Ghaziabad | [54 empty] | Bought Out
Name of Work:-Works at proposed increasing capacity of 33/11KV Substation Bharat Udyog Murad Nagar, Ghaziabad from (1x10)MVA to (10+5)MVA | [54 empty] | Direct
Tender Reference No : 03/2022-23/E.D.C/GZB | [54 empty] | Quote for Supply Portion only
Bidder Name : | [54 empty] | Quote for Erection Portion only
PRICE BID 1. This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns after validating the sheet, else the bidder is liable to be rejected for this tender. 2. Bidders are allowed to enter the Bidder Name and Unit Ex-Works Price and GST in %age only. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents. 9. BIDDERS MUST FILLED UP THE GST IN %AGE OTHERWISE G.S.T. RATES WILL BE TREATED AS INCLUDED IN THE GIVEN BASIC RATES.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Description of Works | Item Code | Tendered Quantity | Unit | Estimated Rate | Bought-out /Direct | Specify Bought-out /Direct | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Ex-Works Price (Rs./Unit) | Excise Duty (Rs/Unit) | CST/VAT (Rs/Unit) | Other Taxes & Duties (Rs/Unit) | Freight & Insurance Charges (in Rs./Unit) |  |  | Unit FOR Dest. Supply Price incl. all Taxes and Duties (in Rs./Unit) (F+G+H+I+J) | Total Value for work (In Rs.) (C x F) | GST (in %age) | Total Value for GST (in Rs.) (F*M/100) |  |  | Total Unit Price incl. GST (in Rs.) (F+N) | [26 empty] | Total Amount excl. GST (in Rs.) (C x F) | Total Amount incl. GST (in Rs.) (C x O) | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Line/ Bus Isolator Structure Fabrication of structure, including cutting, straightening & drilling of holes in Channel/Angle | item1 | 2 | Set. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [8 empty] | 18 |  | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2 | Excavation of earth 2x(1.10x0.60x1.00) | item2 | 2.64 | Cum. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
3 | Supply & fixing of stone pad of size 300x300x75mm | item3 | 8 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
4 | Erection of Line / Bus isolator structure in proper alignment | item4 | 2 | Set. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
5 | Grouting of structure in C.C ratio 1:3:6 2x(1.10x0.60x1.00) | item5 | 2.64 | Cum. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
6 | Making plinth by C.C ratio 1:3:6, in size 2x(1.10x0.60x0.30) | item6 | 0.8 | Cum. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
7 | 12mm thick plastering on plinth in ratio 1:4 of size 2x(1.10x0.30)x2+2x(0.60x0.30)x2+2x(1.10x0.60)x1 | item7 | 6.72 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
8 | L.A.'s, P.I.'s, Unit structure:- Fabrication of structure, including cutting, straightening & drilling of holes in Channel/Angle | item8 | 7 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
9 | Excavation of earth 7x(0.45x0.45x1.00) | item9 | 1.417 | Cum. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
10 | Supply & fixing of stone pad of size 300x300x75mm | item10 | 14 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
11 | Erection of L.A. & Post Insulator structure in proper alignment | item11 | 7 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
12 | Grouting of structure in C.C ratio 1:3:6 7x(0.45x0.45x1.00) | item12 | 1.417 | Cum. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
13 | Making plinth by C.C ratio 1:3:6, in size 7x(0.45x0.45x0.30) | item13 | 0.425 | Cum. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
14 | 12mm thick plastering on plinth in ratio 1:4 of size 7x[(0.45x0.30)x2+(0.45x0.30)x2+(0.45x0.45)x1] | item14 | 5.18 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
15 | C.T's, Fuse Set Unit structure:- Fabrication of structure, including cutting, straightening & drilling of holes in Channel/Angle | item15 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
16 | Excavation of earth 2x(0.90x0.50x1.00) x1 | item16 | 0.9 | Cum. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
17 | Supply & fixing of stone pad of size 300x300x75mm | item17 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
18 | Erection of C.T. & Fuse Set structure in proper alignment | item18 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
19 | Grouting of structure in C.C ratio 1:3:6 2x(0.90x0.50x1.00)x1 | item19 | 0.9 | Cum. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
20 | Making plinth by C.C ratio 1:3:6, in size 2x(0.90x0.50x0.30)x1 | item20 | 0.27 | Cum. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
21 | 12mm thick plastering on plinth in ratio 1:4 of size 2x[(0.90x0.30)x2+(0.50x0.30)x2+(0.90x0.50)x2] | item21 | 3.48 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
22 | 33KV Cable laying. Digging of Cable Trench of size 1050mmx750mm, for laying of 33KV, 3x300Sq.mm. Cable, along the Road. | item22 | 80 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
23 | Safe laying of 33KV, 3x300Sq.mm. XLPE Cable in Cable Trench to respective Double Pole. | item23 | 160 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
24 | Providing & Laying of Ist Class Bricks, along the length on both side of 33KV XLPE Cable in Cable Trench (minium 27No. Bricks/Mtr per Cable) and Stone Slab of size 450x600x50mm on top of the each Cable, including providing & filling River Sand inside the Bricks as per specification. | item24 | 80 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
25 | Back filling of excavated earth in the cable trench upto the ground level and ramming properly. | item25 | 80 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
26 | Making of 33KV Outdoor type cable end termination by heat shrinkable XLPE Cable Jointing Kits and crimping with proper size aluminium lugs. Work includes providing Aluminum lugs, insulating tapes etc as per specifications. | item26 | 10 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
27 | Laying of 33KV, 3x300Sq.mm XLPE Cable in the air and mounting and clamping 2No. 33KV XLPE Boxes on double pole/M.S. structure and making connection with 33KV over head line at both ends. | item27 | 60 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
28 | Providing and fixing 150mm dia 2mm thick 3M long G.I.Pipe over 33KV, 3x300Sq.mm XLPE Cable before mounting the 2No. Cable on double pole. Work includes fixing of Clamp, sealing of top and bottom end of the G.I.Pipe. One end of G.I.Pipe is to be buried under earth about 500mm. | item28 | 10 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
29 | Earthing of Outdoor Equipments in Switchyard, details as given below:- Digging of Trench of size-0.50x0.75x30M.,for laying of Earth mat throughout in switchyard and re-filling &ramming of the same earth in the to the trenches after completion of earth mat work. | item29 | 11.25 | Cu.M. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
30 | Laying of 32mm.dia M.S.Bar in Trench, properly in alignment along the length and width in switchyard. | item30 | 30 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
31 | Cutting of 32mm.dia M.S.Bar-3M.long and making one end in conical shape, by forging process and driving it into the earth, in trench at fixed distance as per drawing and properly welding with M.S.Bar Earthmat. | item31 | 10 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
32 | Proper continuous electric welding of overlap joints of M.S.Bar upto a length of 150mm. On both sides,along the length of M.S.Bar and an extra piece of 12mm M.S.Round-150mm.long, providing on both sides of Overlap Joints and continuous electric welding on both side, along the length of M.S.Bar. All joints shall be painted with black bituminous paint. | item32 | 6 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
33 | Proper electric welding at X-joints of M.S.Bar and welding by providing 25x6mm.”U” type Clamp of M.S.Flat, and proper continuous electric welding with M.S.Electrode and M.S.Bar at each X-joints. All joints shall be painted with black bituminous paint. | item33 | 10 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
34 | Providing & laying of G.I.Strip of size 50x6mm for connecting the earthmat with each equipment (Terminal Gantry, Bus Gantry, Bus Isolators, Line Isolator, 33KV C.T., 33KV V.C.B., L.As., Fuse Set, Post Insulators, T/F Body & its neutral and M.S.Frame of Cable Supporting Structure), various steel structures. The work also includes cutting, bendidng, straightening, over-laping and welding the earth strip with earth mat and by using high quality arc welding in already digged trenches. | item34 | 60 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
35 | Earthing of indoor equipment, details as given below:- Cutting of 32mm.dia M.S. Bar-3Mtr.long and making one end in conical shape by forging process and driving it into the earth at each corner of bridge outside control room and proper welding with M.S.Bars. | item35 | 8 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
36 | Digging of Pits for making Bridge on both side of control room by laying 32mm. dia M.S.Round in rectangular shape. Electric welding on cross joints by providing “U” Clamp in size 25x6mm. of M.S.Flat and inter connecting both by M.S.Round 32mm.dia through control room trench, with over lap joint by providing M.S.Round-12mm dia, on both sides of over lap joints of M.S.Round, by electric welding. All joints shall be painted with black bituminious paint. | item36 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
37 | Making earthing of all 11KV Switchgears, C.T. and other equipments on both earth terminal inside the control room by providing G.I.Strip in size 50x6mm. with 32mm. dia M.S.Round laid in trench with proper electric welding. | item37 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
38 | Painting of G.I.Earth Strip of size (50x6) mm with two coats of ISI mark synthetic channel green paint. | item38 | 60 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
39 | Supply of G.I. Strip size 50x60mm for earthing of outdoor & indoor equipment | item39 | 60 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
40 | Erection of 11KV Switchgears in proper alignment, in Control Room, including safe shifting, from Dump Place. Making 4No. Pockets for each and providing/fixing of Reg Bolt by CC in ratio 1:2:4, with tightening also, including safely mounting of 11KV P.T. on 11KV I/C Switchgear, filling of oil (if required), making all electrical connections. 11KV Incoming VCB 600/300/5A, 350MVA | item40 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
41 | 11KV Bus Couplar 350MVA | item41 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
42 | Proper fixing & making bus bar connection in between two switch gears after proper cleaning. Work also include proper insulation, taping by empire, PVC and H.T. taps etc. | item42 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
43 | Supply & fabrication of copper bus bar of size (1500x50x6)mm for proper fixing between two switchgear after proper cleaning | item43 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
44 | Plinth for 5 MVA Transformer Construction of plinth for 5 MVA, 33/11 KV Transformer of (3.46x4.46x1.0)m (0.50m below ground level and 0.5 m above ground level) as per details & drawing attached:- Excavation of earth (3.7x4.7x0.5)m | item44 | 8.69 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
45 | Flooring of plinth in C.C. 1:4:8 (cement, sand & brick ballast) for making foundation bed. Size (3.7x4.7x0.15)m. | item45 | 2.6 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
46 | 1st Class brick work for side walls size 0.345 m wide upto 0.3m height and 0.23 m wide upto 0.35 m height cm C.C. ratio of 1:4 (cement & fine sand) | item46 | 2.85 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
47 | Filling of brick ballast in plinth in ratio 1:4:8 (cement, coarse sand & brick ballast) with proper ramming. Size (3.0x4.0x0.65)m. | item47 | 7.8 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
48 | R.C.C. work on the top of plinth in ratio 1:2:4 in (3.46x4.46)m size and 0.20m in thickness by using M.S. Tor of 12 mm dia. 12 Nos. in each direction across to each other. The work also includes cutting, bending of M.S. Tor etc. and all required decentrilised material provided by contractor own his cost. | item48 | 3.08 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
49 | Quantity of M.S. Tor of size 12 mm dia required for reinforcement of plinth in R.C.C. work, work also includes cutting, winding and laying etc. in the T/F plinth. | item49 | 240 | Kgs. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
50 | Grouting of 02 Nos. 90/105 lb. Rail pieces of 3.46m long and (50x50x6)mm M.S. Angle in R.C.C. work at the top of plinth work also includes cutting of rail and angles pieces etc. | item50 | 7 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
51 | 12mm thick plaster with cement mortar ratio 1:4 (cement & fine sand) of plinth of 0.4m upper side. | item51 | 18 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
52 | Plinth for 33 KV V.C.B. Construction of plinth for the structure of 33 KV VCB & C.T.'s as per details for 01 No.:- Excavation of earth of size (2.4x1.5x1.0)m pits for construction of plinth. | item52 | 3.6 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
53 | Brick Ballast ratio (1:4:8) (cement, sand & brick ballast) for foundation work (2.4x1.5x0.15)m plinth. | item53 | 0.54 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
54 | R.C.C. work in ratio 1:2:4 cement, coarse sand & stone Ballast of 20mm size for making plinth of size (2.4x1.5x1.0)m and grouting of foundation bolts 04 Nos. for 33 KV VCB. | item54 | 3.6 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
55 | 12mm thick plaster with cement mortar in ratio 1:4 (cement & fine sand) of plinth of 0.4m upper side size (2.4x1.5x0.4)m. | item55 | 6.72 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
56 | Construction of Control cable trench as per details Excavation of earth in size 0.650x0.40m.x30Mtr | item56 | 7.8 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
57 | C.C. work in foundation in ratio 1:3:6 (cement, sand & stone grift) with proper ramming in size 0.65x0.15 mtr.) | item57 | 2.92 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
58 | First Class Brick work in cement mortar in ratio 1:4 in size 0.115/0.23x0.32 Mtr. | item58 | 2.25 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
59 | 25mm thick C.C. in floor of Cable Trench in ratio 1:2:4 (cement, coarse sand and stone grift) 20mm gauge in size 0.3 mtr. width. | item59 | 9 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
60 | Providing & Grouting of M.S. Strip of size 450x25x6mm in cable trench 100mm above floor level and at equal space distance 300mm. | item60 | 90 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
61 | Grouting of M.S. Angle Iron of size 50x50x6mm in upper edge of trench. | item61 | 82.5 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
62 | Plastering of Trench in Cement, Mortar in ratio 1:4, 12mm thick in cable trench. | item62 | 34.26 | Sqm | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
63 | Fabrication and fixing cable trench cover of M.S. Angle Iron size 50x50x6mm of size 0.3m wide 0.5 to 1.0 mtr. length with proper welding of 8 mm size of bar 2 Nos. in length and 6 Nos. in width. M.S. Bar & RCC materials provided by the contractor. (i) 0.5 Mtr. long | item63 | 10 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
64 | (ii) 1.00 Mtr. long | item64 | 25 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
65 | Painting of Structures Painting of the following structure with one coat of ready mixed primer and two coats of ISI Mark Aluminium paint after rubbing with sand paper to the surface of the structure including labour and T&P complete in all respect. Bus Bar Gantry Structure | item65 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
66 | Line Isolator, Bus Isolator, Post Insulator, Fuse Set and L.A's & CT unit, cable support structure. | item66 | 9 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
67 | Cable support structure and Neutral support structure, Copper Bus Bar Support Structure &M.S.Frames. | item67 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
68 | Double Pole Structure | item68 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
69 | Installation of 33/11 KV, 5 MVA Transformer Safe Shifting of 5 MVA, 33/11 KV Transformer from outside of switch yard to transformer plinth in Switch Yard. | item69 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
70 | Erection of shifted Transformer at plinth by fixing all accessories like radiators, conservator tank, filling the transformer oil to desired level and ensuring that there is no leakage, complete job in all respect. | item70 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
71 | Water level earthing by Boring and lowering of G.I. pipe size 40 mm dia & thickness 2mm into the ground at 20 Mtr depth or upto the water level with the lower end of solid copper cone Approx 225 mm long and 750 gm in weight shall be provided and screwed in pipe as well as bringing out a continuous copper wire 6 SWG from the cone up to the ground surface where it will be bolted to the M.S. earth Strip for Transformer neutral connection, the earth strip will be welded to the G.I. pipe and neutral earthing support all required material provied/supply by contractor own in cost. | item71 | 5 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
72 | Fabrication and erection of neutral earthing L Type support made of M.S. Channel size 100x50mm. Structure shall be 4 Mtr. long with 1 Mtr. Arms. Structure shall be grouted in ratio 1:3:6 in block size 300x300x700mm and painted with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint work includes connecting neutral bushing rod of power Transformer and M.S. Earthing strip with the help of flexible copper bond, M.S. Bolt and washer with stone Pad of size (300x300x75mm). | item72 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
73 | Fabrication and erection of cable support made of two pieces of M.S. Channel (100x50x6)mm, 2.75 meter long, joined to each other by means of 5 Nos. M.S. Angle (50x50x6) mm pieces of size 0.5Mtr long each by welding at equal intervals and grouting in a block of size (300x300x700)mm in C.C. 1:3:6 complete with one coat of ready mixed primer and two coats of Al. paint. Work includes providing of three Nos. M.S. clamps made of (50x6)mm M.S. Flat for holding the cable including nuts and bolts with stone Pad of size (300x300x75mm). | item73 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
74 | Fabrication and grouting of M.S. frames 3.60 mt. long for support of copper Bus Bar. Bus Bar will be provided in L.V. side of Power transformer. The M.S. frame shall be made of M.S. channel (100x50)mm in 'T' shape. Providing 2 Nos. support of M.S. Angle iron (50x50x6)mm, 0.60mt. long below the top channel, drilling of 3 Nos. hole on the top channel for fixing of 11 KV pin insulator. The M.S. frame shall be painted with one coat of primer & two coat of aluminium paint and grouting the frame in C.C. ratio 1:3:6 in a block of size (300x300x700) mm with stone Pad of size (300x300x75mm). The work also includes the fixing of 3 Nos. 11 KV pin insulator with pin and binding the copper Bus Bar with the pin insulator by Aluminium binding wire in complete. | item74 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
75 | Supply & Fabrication of copper bus bar of size (2500x50x6)mm in L.V. side of 5 MVA 33/11 KV, power transformer, Work includes connection of outside bus bar in L.V. side busing rod of Power Transformer and other side with outdoor 11 KV cable box as well as providing empire tape and H.T. tape etc. for proper insulation work. | item75 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
76 | H.T. Power Cable Laying: Laying 11 KV, (3x300) mm2/(3x400) mm2 XLPE, Cable from power transformer to 11 KV incoming switch gear in the cable trench 0.45 m wide, 0.90m depth. Providing 150 mm local sand for cushion beneath and 150 mm above the cable (quality of local sand required 0.375 cum/m in length). The cable shall be dully protected by brick. On both side of cable by laying brick vertically and bricks would also be laid bricks along the cable (minimum 18 Nos. of bricks are to be laid top and outer side along the cable. The work includes digging of trenches, laying of cable in under ground trenches, joining of terminal's, back filling of earth and testing and commissioning of power cable etc. Spare cable shall be left over and laid in the trenches in shape of 6 m ring at both ends. | item76 | 80 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
77 | Laying and dressing of 11 KV 3x300 mm2/3x400 mm2 power cable in air/Trench. | item77 | 20 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
78 | Laying of 11KV XLPE cable of size 3x185mm² details as given below. Digging of trench of size 700x1000mm for laying of 11KV cable by making loops. | item78 | 80 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
79 | Supply & filling 150mm thickness local sand for cushion beneath and 150mm above the cable quantity with local sand. | item79 | 80 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
80 | Safely laying of 02Nos. (Double Ckt) 11KV 3x185mm² XLPE cable in cable trench/Loop | item80 | 160 | RMT. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
81 | Laying of Ist class bricks along the length of cable on both sides and fixing stone slab 550x400x40mm as a top cover over the laid XLPE cable in trench. (27 Bricks Per Meter) | item81 | 80 | RMT. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
82 | Back filling of excavated earth in the cable trench up to the ground level and ramming properly. | item82 | 80 | RMT. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
83 | Laying of 11KV, 3x185Sq.mm XLPE Cable in the air and mounting and clamping 2No. 33KV XLPE Boxes on double pole/M.S. structure and making connection with 33KV over head line at both ends. | item83 | 60 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
84 | Providing and fixing 150mm dia 2mm thick 3M long G.I.Pipe over 11KV, 3x185Sq.mm XLPE Cable before mounting the 2No. Cable on double pole. Work includes fixing of Clamp, sealing of top and bottom end of the G.I.Pipe. One end of G.I.Pipe is to be buried under earth about 500mm. | item84 | 6 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
85 | Construction of 11 KV Double Poles: Erection and grouting of 4 Nos. STP-55-11Mtr long for making DP Structure including fabrication fixing of M.S. Channel, M.S. Angle, TPMO, Fuse Set, disc, insulators, pin insulators etc. the work includes supply and fixing of necessary clamps with nuts, bolts and washers. The work also includes grouting of Double pole support in C.C. 1:4:8 (cement, sand & brick ballast) in block of size (0.45m x 0.45 x 1/6 length of the pole) including earthing of Double pole with M.S. earthing rod complete in all respect. | item85 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
86 | Erection and grouting of 2 Nos. PCC 9.0Mtr long for making DP Structure including fabrication fixing of M.S. Channel, M.S. Angle, Fuse Set, disc, insulators, pin insulators etc. the work includes supply and fixing of necessary clamps with nuts, bolts and washers. The work also includes grouting of Double pole support in C.C. 1:4:8 (cement, sand & brick ballast) in block of size (0.45m x 0.45 x 1/6 length of the pole) including earthing of Double pole with M.S. earthing rod complete in all respect. | item86 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
87 | Making plinth of D/P support in CC 1:3:6 of size 45 cm dia & .30 mtr. In height complete with all labour T&P etc. | item87 | 6 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
88 | Preparation of 11 KV Power Cable ends: Making of 11 KV XLPE Heat shrinkable Out door jointing kits after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs. | item88 | 8 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
89 | Making of 11 KV XLPE heat shrinkable indoor jointing kits in switch gears after carefully removing the insulation of cable, providing and crimping of proper size of lugs, plumbing and taping of cable with good quality available insulation tape with J/Kit boxes, Fixing and insulating of lugs on cable with switch gear complete in all respect. | item89 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
90 | Installation of 24V Battery and Battery Charger: Assembling and installation of the cabinet of 24V battery and battery charger in switch gear control room including grouting of foundation bolts as per drawing of manufacture, including providing the foundation nuts and bolts of proper size. The electrical connection between battery and battery charger with flexible copper lead of size 7/20 SWG shall be provided & done properly by the contractor. The work includes installation, wiring upto control panel, testing and commissioning complete in all respect. | item90 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
91 | Provding & Laying of 2x2.5mm2 control cables I.S mark i.e. from Buchholz realy to Marshalling box Marshalling box to indication protection board in switch gear room, 33 KV CT's to CT's Junction Box, CT 33 KV, V.C.B. Control Panel Junction Box to 33 KV VCB control panel and control panel to 33 KV VCB outdoor operating mechanism panel from T/F etc. in the cable trench including making proper connection at Buchholz Relay, Marshalling box and indication board as per required for installed equipment. | item91 | 200 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
92 | Providing & Laying of 4x2.5mm2 control cables I.S mark i.e. from Buchholz realy to Marshalling box Marshalling box to indication protection board in switch gear room, 33 KV CT's to CT's Junction Box, CT 33 KV, V.C.B. Control Panel Junction Box to 33 KV VCB control panel and control panel to 33 KV VCB outdoor operating mechanism panel from T/F etc. in the cable trench including making proper connection at Buchholz Relay, Marshalling box and indication board as per required for installed equipment. | item92 | 400 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
93 | Installation of 33 KV Lightning Arrestors: Installation of 33 KV Lightning Arrestors: Assembling and installation/mounting of 3 Nos. lighting arrestors on the L.A.'s structure/terminal gentry, complete with earthing and line connections. The work includes fabrication for proper fixing, if required. | item93 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
94 | Installation of 33 KV Post Insulators: Installation of 3 Nos. PI on structure. The work includes fabrication for proper fixing, if required. | item94 | 36 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
95 | Installation of 33 KV Fuse Set: Assembling and installation of fuse set on the fuse set structure. The work includes fabrication for proper fixing, if required. | item95 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
96 | Installation of 33 KV VCB Assembling and installation of 33 KV VCB on the VCB out door structure on the plinth. Adjustment of operating mechanism in proper alignment for smooth operation of the same. The work also includes fabrication of addition arrangement for proper fixing, if required. | item96 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
97 | Installation of 33 KV C.T.'s: Installation of 3 Nos. C.T.'s on the C.T's structure. The work includes fabrication for proper fixing, if required to complete the work. | item97 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
98 | 33 KV CT's Junction Box: Providing & fixing of junction box of size (400x400x150) mm made of M.S. sheet of 16 SWG in between 33 KV CT's & control panel. The work also include making proper connection on the junction box and making all connection in between CT's and control panel complete as per manufacture's panel drawing including testing and commissioning of work etc. complete the work. | item98 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
99 | Installation of 33 KV VCB Control Panel Carefully and safely shifting of 33 KV VCB control panel from outside of the switch gear room to inside of the switch gear room, grouting with anchor bolts in the floor, work also includes cutting & proper finishing of floor if necessary for completion of work. Placing and fixing of panel on foundation, bolts of proper size in proper position and alignment. | item99 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
100 | 33 KV Bus Bar Jumpering: Jumpering, including clamping/binding with ACSR Dog conductor: 33KV Post insulator structure to 33KV isolator structure. | item100 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
101 | 33KV isolator to 33KV Post insulator | item101 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
102 | 33KV Post insulator to 33KV isolator structure. | item102 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
103 | 33KV isolator structure to 33KV Post Insulator | item103 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
104 | 33KV Post Insulator to 33KV VCB | item104 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
105 | 33 KV VCB to 33KV C.T | item105 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
106 | 33 KV CT to 33KV Fuse set | item106 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
107 | 33KV Fuse set to 33 KV L.A. | item107 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
108 | 33 KV L.A. to 33/11 KV Power T/f | item108 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
109 | Construction of S.S.Os. Approach Road-1.2M wide in switch yard by laying dry brick-ballast in 15Cm layer, 115mm thick brick work 1:4 in both side of edge, providing 10Cm thick CC in ratio 1:2:4. the work includes proper plastering top & side of road and making groove, leveling & dressing of earth beneath the brick work on edge. | item109 | 30 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
110 | To provide required No. of technicians with proper testing equipments to work on power T/f, HT/LT panels during testing as assisting technical hands of test team during commissioning & energisation. | item110 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
111 | Loading, Safe carriage & unloading of following stock material from any stores centres under PVVNL, depending upon the availability of material at Stores Centres, with loading & unloading at both ends respectively. M.S. Steel, 7 Mtr long Rail Pieces, M.S. Angle, M.S. channel, Conductor, M.S.Round etc. | item111 | 4 | MT. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
112 | Bus/ Line isolator | item112 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
113 | 11 KV Switch gear | item113 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
114 | L.A. | item114 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
115 | Fuse set | item115 | 1 | Set. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
116 | 33 KV VCB | item116 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
117 | C.T. | item117 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
118 | 33 KV control panel | item118 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
119 | 11 KV Cable 3x185mm2 | item119 | 220 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
120 | 11 KV Cable 3x300mm2 | item120 | 100 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
121 | 11KV cable J/kit 3x185mm² / 3x300mm² | item121 | 12 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
122 | STP-SP-55-11Mtr | item122 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
123 | PCC Pole 9.0Mtr | item123 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
124 | 33KV Post insulator | item124 | 36 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
125 | 33 KV Cable 3x300mm2 | item125 | 220 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
126 | 33KV cable J/kit O/D 3x300mm² | item126 | 10 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
127 | 24 Volt Battery & Battery Charger | item127 | 1 | Set. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
128 | ACSR Dog Conductor | item128 | 80 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
129 | Fresh T/F oil | item129 | 418 | Ltr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
130 | Safe Dismantling, Shifting, Loading, Carriage from ESC to site (with in 100Km PVVNL area) Unloading of 5MVA T/F | item130 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
131 | Safe Dismantling and Shifting of 11KV VCB panel in control room & Re-installation in control room at new place. | item131 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
132 | Safe Dismantling and Shifting of 11/0.4KV LT 25KVA transformer from old double Pole and Re-installation on new erected double Pole. | item132 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
133 | Safe Dismantling of old double Pole (03 No.), 25Mtr Overhead 33KV line & 25Mtr Overhead 11KV line. | item133 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
134 | Removal of old steel structure of P.I. in switchyard | item134 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
135 | About 08 Mtrs wall breaking for shifting of 33/11KV, 05MVA T/F from outside to inside of switchyard & after this rebuild of boundary wall. | item135 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
136 | Re-arrangement of old 11KV cable & cattereds in the switchyard & in control room. | item136 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
137 | Safe carriage of old material received back material from site to store including loading & unloading at both ents. | item137 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
138 | Providing & Laying G.I.Pipe 150mm dia (I.D-146mm, OD-1500mm thickness 2mm at nala crossing | item138 | 12 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
Total in Figures | [51 empty] | 0 | 0 |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [7 empty] | % | [39 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information