## PVVNL-MT/COM/32(s)/21-22

TECHNICAL SPECIFICATION FOR 33 KV PTs

- GENERAL:

  - This specification covers the design, manufacture testing and supply of 33 KV PT.

  - The PT shall comply with the requirements of the relevant I.S. specifications.

  - List of raw material to be along with the name of suppliers should be submitted with the 	tender.

2.0	ELECTRICAL COMPONENTS:

The supplier shall be original manufacturer of the epoxy resin cast PT or accredited representative of such manufacturer. The bidder must have facility to cast epoxy resin by hot casting process under vacuum for PTs at his own works. These PT should have been type tested as per relevant ISS (latest revision) in a Govt. accredited National Test House such as CPRI, Bangalore / Bhopal etc. during the last five years from the date of Tender opening. A brief detail of the various components to be provided in the metering cubicle is give below:-

3.0         POTENTIAL TRANSFORMER:

The primary and secondary winding of 33 KV PT should be wound on insulating craft paper. These will be dry type Epoxy resign cast, air cooled conforming to IS: 3156/1992 or latest amendment thereof. Entire PT assembly i.e. core and coil should be encapsulated under vacuum impregnation in epoxy resin. The PTs shall have a ratio of 33 / √3 KV / 110 / √3 V and with a rated burden of 25 VA and of accuracy class 0.5. The material of primary and secondary winding should be copper. The cross sectional area of primary should be 0.015 sq. mm(Minimum) and that of secondary winding should be 1.6 sq. mm (Minimum). These will be connected in star-star formation for phase-to-phase voltage ration of 33 KV/110 V. There will be no HT fuses in the primary side and secondary side of the potential Transformer. Rated voltage factor of PT should be as per ISS. Potential transformer should have been type tested as per IS: 3156/1992 or latest version thereof

  - INSULATORS:

The insulators if required for all the bus supports shall be epoxy resin cast, indoor type. The hardware used shall be electroplated M.S. The insulators shall be conforming to relevant ISS.

3.2      PT LINKS:

The bus –bar and HT side of PT shall be connected through a flexible copper strip of size 25mm X 3.5 mm X 0.5 mm or 8 SWG Copper Wire such that HT Terminals of PT are not subjected to any compression or tension forces.

3.3	L.T. WIRES:

The LT wiring shall be done with PVC insulated flexible copper wires of cross wires of cross section not less than 2.5 Sq. mm. of reputed make, conforming to relevant ISS. These will be provided with lugs and ferrules at termination in the LT Compartments, suitable colour, code, PVC insulated flexible Copper (without joints) will be neatly bunched and dressed and without any joints should be used. These wires shall connect secondaries of PT. Proper code and numbers should be marked on ferrules for individual PT connections.

3.4	MAKE OF THE COMPONENT:

List of raw material to be used along with names of the suppliers should be submitted 	with Part-I of the tender. Make of various components as detailed above and as being 	given below.

3.5	HARDWARE:

Hot-Dip Galvanized of any standard make.

3.6	PAINT:

Epoxy – Paint of standard make.

3.7      EPOXY RESIN: –

Dr. Beck, Huntsman, Atul.

4.0	INSPECTION AND TESTING:

All PTs shall be inspected and tested at manufacturer works to verify that these are being supplied in accordance with relevant standards. Technical Specification, Guaranteed Technical Particulars and acceptance and routine tests.

Inspection of material offered for inspection shall be carried out jointly by the representative of Superintending Engineer (Quality Cell), PVVNL, Meerut.

While offering for inspection / testing confirming to the effect that the cubicle have successfully withstand the routing tests (along with test results)  is required to be submitted for each lot offered for inspection SE (Quality Cell), PVVNL, Meerut.

All instruments used in inspection and testing should be properly calibrated and sealed once a year. Calibration certificate when demanded by the inspecting officer shall be provided / produced for verification purpose. In case of any dispute regarding calibration, instruments shall be sealed and singed by the representative of the supplier and purchaser and will be sent to test house / Govt. Lab / Govt. institution of repute, for calibration at the cost of supplier. The result of such testing shall be binding on the supplier.

Purchaser reserves the right to get the PT's  inspected / type tested before dispatch by any independent inspection agency at the cost of purchaser in case the equipment with stand the type test, otherwise the supplier has to bear such cost in addition to any other action deemed appropriate by the purchaser.

One sample of PT of any ratio randomly selected from each offered lot, shall be opened for verifying the diameter & cross sectional area of primary coil conductors including verification of GTP

Testing Facility: - The manufacturer must have testing facilities at their works as per clause No. 1.2.3 of "Instruction to Tenderer" to carry out all the routine & acceptance test (including partial discharge test) as mentioned below. List of Testing equipment with photo copy of calibration certificates should be enclosed with Part- I of the tender.

Schematic drawing showing each and every details, dimensions and wiring diagrams shall be submitted necessary for each type of metering cubicle.

4.1	Type test:

All the type tests as listed below shall be carried out for the equipment strictly as described as per the relevant ISS(or latest amendment thereafter).

4.1.2	Potential Transformers: (As per IS: 3159 / 1992 or its latest amendment. Type test on PT shall be done on any one unit

- Determination of error according to the requirements of accuracy class.

- Temperature rise test.

(i) At 1.2 times of rated voltage for continuous period.

(ii) At 1.9 times of rated voltage for 30 second.

- Impulse Voltage Test.

4.2	Routine Tests: -

The following shall constitute the routine test and acceptance tests.

4.2.1	Potential Transformers:

- Verification of terminal markings and polarity

- Power frequency dry withstand test on primary windings.

- Power frequency dry withstand test on secondary windings.

- Determination of error according to the requirements of appropriate accuracy class.

- Partial discharge test in accordance with IS: 11322 / 1985

4.3	Acceptance Test:

4.3.1 	Dimensional check of metering cubicle

High voltage power frequency test on primary winding at 70 KV for one minute and secondary winding 3 KV for one minute for metering cubicles.

4.4	Potential Transformers

- Verification of terminal markings and polarity

- High Voltage power dry withstand test on primary windings.

- High voltage power dry withstand test on secondary windings.

- Determination of error according to the requirements of appropriate accuracy class.

- Temperature rise test

(i) At 1.2 times of rated voltage for continuous period.

(ii) At 1.9 times of rated voltage for 30 second.

- Partial discharge test

5.0	In case of any discrepancy between specification and relevant standard, provision 	contained in this specification shall prevail.