## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle, Hapur.
Name of Work: FOR CONSTRUCTION OF ELECTRICITY LINE AND OTHER ASSOCIATED WORKS FOR RELEASING CONNECTION TO ARVIND DAIRY PVT. LTD. (SHRI LALIT MOHAN GUPTA VILLAGE-DHAULANA HAPUR), IN DEPOSIT SCHEME, IN THE JURISDICTION OF EDD-II HAPUR, UNDER EDC., HAPUR.
Tender No: 23(W)/EDCH/2022-23
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | FOR CONSTRUCTION OF ELECTRICITY LINE AND OTHER ASSOCIATED WORKS FOR RELEASING CONNECTION TO ARVIND DAIRY PVT. LTD. (SHRI LALIT MOHAN GUPTA VILLAGE-DHAULANA HAPUR), IN DEPOSIT SCHEME, IN THE JURISDICTION OF EDD-II HAPUR, UNDER EDC., HAPUR. (All work will be done as per Sanctioned estimate) | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Carriage of line material (like 11KV Cable Jointing Kit indoor/outdoor type, clamps, channel, conductor etc.) from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001113 | 31.35 | Qtl. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Carriage of PC Pole 8.5 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 95 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.03 | Carriage of 11KV VCB from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | Carriage of 11KV CT/PT Unit from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.05 | Carriage of Metering Cubical Set Complete, from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.06 | Carriage of 11KV XLPE Cable 3x70sqmm, from Electricity store center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 3800 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.07 | Erection & Fixing of PCC Pole 8.5 mtr. long in 11 KV line after digging of suitable pits including fixing of requisite accessories as per RESPO Drawing/Norms by providing F-Bracket made of M.S. Flat of size 50x6 mm, Cross Arm holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 69 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.08 | Fabrication, erection and fixing of double pole on PCC Pole 8.5 mtr. long with fixing of M.S. Top & Dropper Channel, M.S. S/S Angle, E-Bracket, 11 KV Pin insulator with Pin, Disc Insulator with Disc fitting as per RESPO Drawing/Norms by providing top and dropper clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 13 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.09 | Installation of 11KV VCB Completion of properly work as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.1 | Installation of 11KV Metering Cubical Complete work as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | Mounting, Placing and connecting from LT/HT side of 11KV, CT/PT Units as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 2 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | Laying of 11KV XLPE Cable 3x70Sqmm. (Double Circuit 1860x2=3720mtrs.) spare cable shall be left in the loop shape at both ends as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 3720 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | Laying of 11KV XLPE Cable 3x70Sqmm. undergound Trenchless (Double Circuit 40x2=80mtrs.) spare cable shall be left in the loop shape at both ends as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 80 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | Laying, Stringing and final sagging of ACSR Weasel Conductor after binding from Insulator, as per RESPO/Drawing Norms. | BI01010001010000000000000515BI0100001115 | 2000 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | Making and filling of 11KV Cable Jointing Kit 3x70Sqmm, after duly plumbing and taping of suitable XLPE Cable, providing, fixing and crimping of proper size good quality lugs, including cost of lugs and tape etc., as per RESPO Norms. | BI01010001010000000000000515BI0100001115 | 48 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | Providing & Fixing of G.I. pipe 6"dia Class-B over 11KV 3X120Sq.mm XLPE cable before mounting the cable at double pole. The work includes fitting of clamps, sealing of top and bottom of pipe and one end of pipe is to be burried under earth about 500mm earch including mounting and clamping the cable on double pole structure and making connection with overhead line at both ends. | BI01010001010000000000000515BI0100001115 | 32 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.17 | Grouting & fixing of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:4:8 cement, sand, 40mm brick ballast as per drg. Including back filling, proper ramming etc and fixing tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing as per RESPO Drawing/Norms by providing all grouting material and stay clamp made of M.S. Flat of size 50x6mm with proper size bolts & nuts & loops. | BI01010001010000000000000515BI0100001115 | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.18 | Earthing of supports with MS earth Rod of (20x2500)mm long including excavation of pit and driving M.S. Rod 3.0 M apart from support and 0.5m below the ground level and connection below the earth electrodes with the help of G.I. wire & earthing lugs as per RESPO Drawing/Norms by providing proper size nuts & bolts. | BI01010001010000000000000515BI0100001115 | 95 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.19 | Grouting of ST/PCC supports in CC 1:4:8 (Cement, sand & 40mm brick ballast) Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, up to ground level, 300mm plinth above the ground level with CC 1:3:6 (Cement, core sand and Stone grit) with mufting as per drawing, work includes back filling & proper ramming by providing all required grouting materials. | BI01010001010000000000000515BI0100001115 | 95 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.2 | Providing & Fixing of Danger Board, including fixing of all accessories by providing all required materials (like suitable clamps, nuts & bolts etc.) as per RESPO/Drawing Norms. |  | 95 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.21 | Fabrication & Fixing of T-Channel on pole by providing Holding Clamps, F-Clamps & Proper size nuts & bolts, as per RESPO/Norms. |  | 53 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.22 | Wrapping of barbed wire on 11KV ST poles as anti-climbing device for a length of 0.9mtrs. Wire pitch/gap 13mm and fixing upper and lower end keeping lower end at a hieght of 2.75 mtr from the ground complete, including providing & fixing of lower end & upper end clamps made of M.S. Flat 40X5mm complete with nuts & bolts and all other required material and T&P. |  | 95 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.23 | Fabrication of Guarding Angle X Arm & other requisites material for guarding by drawing 02Nos G.I Wire and making loop at suitable distance as per RESPO drawing/Norms by providing holding clamps, 02Nos. Eye bolts made of M.S. round size 12mm dia-100mm long & Cross Arm clamps made of M.S. Flat of size 50X6mm and bolts as per norms of RESPO Lucknow . |  | 360 | mtr. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.24 | Chemical earthing of (MC/CT/PT) Equipment the ground surface where it will be bolted to the M.S. earth strip for connection the earth strip will be welded to the earthing and neutral support, as per RESPO/Norms. |  | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.25 | Jumpering work properly as per RESPO/Norms. | BI01010001010000000000000515BI0100001115 | 2 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information