## BoQ1 (hidden)
Item Wise BoQ
BoQ_Ver3.0 | Item Wise | Normal | INR Only | INR
Select, Excess (+), Less (-)
Tender Inviting Authority: Executive Engineer, Electricity Construction & Works Division, Ghaziabad | [54 empty] | Bought Out
Name of Work:-Works at proposed (1) Increasing capacity of 33/11KV Substation Kilhoda, Hapur (5+10)MVA to (2x10)MVA (2) Increasing capacity of 33/11KV Substation Masoori , Hapur (8+10)MVA to (2x10)MVA (3) Increasing capacity of 33/11KV Substation Delhi Road, Hapur (5+10)MVA to (2x10)MVA (4) Increasing capacity of 33/11KV Substation Jasroop Nagar, Hapur (5+8)MVA to (5+10)MVA | [54 empty] | Direct
Tender Reference No : 115/ECWD/Gzb/2023-24 | [54 empty] | Quote for Supply Portion only
Bidder Name : | [54 empty] | Quote for Erection Portion only
PRICE BID 1. This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns after validating the sheet, else the bidder is liable to be rejected for this tender. 2. Bidders are allowed to enter the Bidder Name and Unit Ex-Works Price and GST in %age only. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents. 9. BIDDERS MUST FILLED UP THE GST IN %AGE OTHERWISE G.S.T. RATES WILL BE TREATED AS INCLUDED IN THE GIVEN BASIC RATES.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Description of Works | Item Code | Tendered Quantity | Unit | Estimated Rate | Bought-out /Direct | Specify Bought-out /Direct | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Ex-Works Price (Rs./Unit) | Excise Duty (Rs/Unit) | CST/VAT (Rs/Unit) | Other Taxes & Duties (Rs/Unit) | Freight & Insurance Charges (in Rs./Unit) |  |  | Unit FOR Dest. Supply Price incl. all Taxes and Duties (in Rs./Unit) (F+G+H+I+J) | Total Value for work (In Rs.) (C x F) | GST (in %age) | Total Value for GST (in Rs.) |  |  | Total Unit Price incl. GST (in Rs.) | [26 empty] | Total Amount excl. GST (in Rs.) | Total Amount incl. GST (in Rs.) | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Carriage of following material from PVVNL Store 33KV Lightening arrester | item1 | 9 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [8 empty] | 18 |  | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2 | 33KV line isolator 800A, | item2 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
3 | 33KV Post insulator | item3 | 12 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
4 | 33KV VCB 1250Amp. | item4 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
5 | 33KV CT 200/100/1-1-1A | item5 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
6 | 33KV Control Panel for single Transformer | item6 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
7 | 33KV Control Panel for double Transformer | item7 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
8 | 11KV XLPE cable 3x300mm² | item8 | 275 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
9 | 11KV Cable J/kit outdoor type for 3x300mm / 3x185mm | item9 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
10 | 11KV Cable J/kit indoor type for 3x300mm / 3x185mm | item10 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
11 | 33KV Fuse set | item11 | 3 | set | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
12 | Loading, Safe carriage & unloading of following stock material from any stores centres under PVVNL, depending upon the availability of material at Stores Centres, with loading & unloading at both ends respectively. Steel, 3.5Mtr long Rail Pieces, Angle channel, Conductor, M.S.Round etc. | item12 | 2.5 | MT. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
13 | Removal of existing 5/8MVA Transformer and other accessories equipments. Disconnecting HT cable connection from 33KV side & 11KV side of 5/8MVA Power transformer for removing power transformer from plinth after proper shutdown. Dismantling of 11KV cable support structure, copper bus bar structure, M.S.Frame etc. | item13 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
14 | Disconnecting copper flexible/Earthing strip from Power transformer neutral & Dismantling neutral earthing system to facilitate removal of Power transformer from plinth. | item14 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
15 | Disconnecting Earthing strip from body of 05/8MVA Power transformer. | item15 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
16 | Draining of transformer oil from conservator, radiators of existing 05/8 MVA T/F, at 33/11 KV S/S into the dry & clean drums and stacking at the safe place in Substation outside of switchyard. Empty drums shall be provided by contractor | item16 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
17 | Removal of conservator, radiators and other accessories from existing 05/8 MVA Power transformer. | item17 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
18 | Safe Shifting of 05/8 MVA Power transformer main body and other accessories from the substation switchyard to outside the switchyard at suitable place assigned by concern J.E/S.D.O (Distribution). | item18 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
19 | Re-assembling of conservator, radiators and other accessories to existing 05/8 MVA Power transformer. | item19 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
20 | Re-filling the transformer oil (old & used in existing 5/8MVA T/F) | item20 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
21 | Installation for 33/11KV 10MVA T/F Safe Shifting of 10MVA, 33/11 KV, Power transformer from out side of switchyard to near Power transformer plinth in Switchyard. | item21 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
22 | Erection & Installation of 10MVA Power transformer on Power Transformer plinth by fixing all accessories like radiators, conservator tank, filling the transformer oil to desired level and ensuring that there is no leakage, complete job in all respect. Reconnecting 2 Nos. earthing strip to transformer body. | item22 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
23 | Providing & Laying of G.I. Earth strip of size 50x6mm for connecting the Earth Mat with steel structure & chain link fencing’s posts. The work also includes cutting, bending, traight-tening, over-lapping and welding the Earth Strip with Earth Mat and various steel structures by using high quality Arc welding in already digged trenches. | item23 | 120 | Mt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
24 | Painting of Earth Strip of size (50x6) mm with one coat of ready mixed primer with two coats of ISI mark synthetic channel green paint. | item24 | 120 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
25 | Water level earthing by Boring and lowering of M.S. pipe size 40 mm dia & thickness 3mm into the ground at 50 Mtr depth or upto the water level with the lower end of solid copper cone Approx 225 mm long and 750 gm in weight shall be provided and screwed in pipe as well as bringing out a continuous copper wire 6 SWG from the cone up to the ground surface where it will be bolted to the M.S. earth Strip for Transformer neutral connection, the M.S.Earth strip size 50x6mm will be welded to the M.S. pipe and neutral earthing support & other installed equipment in switchyard. All required material provided / supply by the contractor own his cost. | item25 | 6 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
26 | Supply & Erection solid copper cone Approx 225 mm long and 750 gm in weight | item26 | 6 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
27 | Fabrication and erection of neutral earthing L Type support made of M.S. Channel size 100x50mm. Structure shall be 4 Mtr. Long with 1 Mtr. Arms. Structure shall be grouted in ratio 1:3:6 in block size 300x300x700mm and painted of welding joint with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint work includes connecting neutral bushing rod of power Transformer and M.S. Earthing strip with the help of flexible copper bond, M.S. Bolt and washer. | item27 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
28 | Fabrication and erection of cable support made of two pieces of M.S. Angle (65x65x6)mm, 2.75 meter long, joined to each other by means of 5 Nos. M.S. Flat (50x6) mm pieces of size 750 mm long each by welding at equal intervals and grouting in a block of size (300x300x700)mm in C.C. 1:3:6 (cement, coarse sand and stone ballast) complete and painted of welding joint with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint. Work includes providing of three Nos. M.S. clamps made of (50x6)mm M.S. Flat for holding the cable including nuts and bolts. | item28 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
29 | Fabrication and grouting of M.S. Frames 3.60 mt. long for support of copper Bus Bar. Bus Bar will be provided in L.V. side of Power transformer. The M.S. frame shall be made of M.S. channel (100x50)mm in ‘T’ shape. Providing 2 Nos. support of M.S. Angle iron (50x50x6)mm, 0.60mt. long below the top channel, drilling of 3 Nos. hole on the top channel for fixing of 11 KV pin insulator and painted of welding joint with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint and grouting the frame in C.C. ratio 1:3:6 (cement, coarse sand and stone ballast) in a block of size (300x300x700) mm. The work also includes the fixing of 3 Nos. 11 KV pin insulator with pin and binding the copper Bus Bar with the pin insulator by Aluminium binding wire in complete. | item29 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
30 | Supply & Fabrication of copper bus bar of size (2500x50x6)mm in L.V. side of 10MVA 33/11 KV, power transformer, Work includes connection of outside bus bar in L.V. side busing rod of Power Transformer and other side with outdoor 11 KV cable box as well as providing empire tape and H.T. tape etc. for proper insulation work. | item30 | 12 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
31 | H.T. Power Cable Laying: Laying 11 KV, (3x300) mm2 XLPE, Cable from power transformer to 11 KV incoming switch gear in the cable trench 0.50 m wide, 0.90m depth. Providing 150 mm local sand for cushion beneath and 150 mm above the cable (quality of local sand required 0.375 cum/m in length). The cable shall be dully protected by brick. On both side of cable by laying brick vertically and bricks would also be laid bricks along the single cable (minimum 18 Nos. of bricks are to be laid top and outer side along the single cable. The work includes digging of trenches, laying of cable in under ground trenches, joining of terminal’s, back filling of earth and testing and commissioning of power cable etc. Spare cable shall be left over and laid in the trenches in shape of 6 m ring at both ends. | item31 | 205 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
32 | Laying and dressing of 11 KV 3x300 mm2 power cable in air/Trench. | item32 | 70 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
33 | Preparation of 11 KV Power Cable ends: Making of 11 KV XLPE Heat shrinkable outdoor jointing kits 3x185Sq.mm/3x300Sq.mm after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs | item33 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
34 | Making of 11 KV XLPE heat shrinkable indoor jointing kits 3x185Sq.mm/3x300Sq.mm in switch gears after carefully removing the insulation of cable, providing and crimping of proper size of lugs, plumbing and taping of cable with good quality available insulation tape with J/Kit boxes, Fixing and insulating of lugs on cable with switch gear complete in all respect. | item34 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
35 | Supply & Laying of different size of (2x2.5)mm2 control cables i.e. from Buchholz realy to Marshalling box Marshalling box to indication protection board in switch gear room, 33 KV CT’s to CT’s Junction Box, 33 KV CT, 33 KV PT, V.C.B. Control Panel Junction Box to 33 KV VCB control panel and control panel to 33 KV VCB outdoor operating mechanism panel from T/F etc. in the cable trench including making proper connection at Buchholz Relay, Marshalling box and indication board as per required for installed equipment. | item35 | 50 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
36 | Supply & Laying of different size of (4x2.5)mm2 control cables i.e. from Buchholz realy to Marshalling box Marshalling box to indication protection board in switch gear room, 33 KV CT’s to CT’s Junction Box, 33 KV CT, 33 KV PT, V.C.B. Control Panel Junction Box to 33 KV VCB control panel and control panel to 33 KV VCB outdoor operating mechanism panel from T/F etc. in the cable trench including making proper connection at Buchholz Relay, Marshalling box and indication board as per required for installed equipment. | item36 | 50 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
37 | Painting of Structures Painting of the following structure with one coat of ready mixed primer and two coats of ISI Mark Aluminium paint after rubbing with sand paper to the surface of the structure including labour and T&P complete in all respect. Painting of Substation Structures | item37 | 4 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
38 | Installation of 33 KV Isolators: Assembling and installation of line/Bus Isolator on the isolator structure. Adjusting of operating mechanism in proper alignment so as to ensure smooth operation of the same. In case of Line Isolator proper operation of earth links shall also be ensured. The work includes fabrication for proper fixing if required. | item38 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
39 | Installation of 33 KV Lightning Arrestors: Assembling and installation/mounting of 3 Nos. lighting arrestors on the L.A.’s structure/terminal gentry, complete with earthing and line connections. The work includes fabrication for proper fixing, if required. | item39 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
40 | Installation of 33 KV Post Insulators: Installation of 3 Nos. PI on structure. The work includes fabrication for proper fixing, if required. | item40 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
41 | Installation of 33 KV VCB Assembling and installation of 33 KV VCB on the VCB out door structure on the plinth. Adjustment of operating mechanism in proper alignment for smooth operation of the same. The work also includes fabrication of addition arrangement for proper fixing, if required. | item41 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
42 | Installation of 33 KV VCB Control Panel for single T/F Carefully and safely shifting of 33 KV VCB control panel from outside of the switch gear room to inside of the switch gear room, grouting with anchor bolts in the floor, work also includes cutting & proper finishing of floor if necessary for completion of work. Placing and fixing of panel on foundation, bolts of proper size in proper position and alignment. | item42 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
43 | Installation of 33 KV VCB Control Panel for Double T/F Carefully and safely shifting of 33 KV VCB control panel from outside of the switch gear room to inside of the switch gear room, grouting with anchor bolts in the floor, work also includes cutting & proper finishing of floor if necessary for completion of work. Placing and fixing of panel on foundation, bolts of proper size in proper position and alignment. | item43 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
44 | Installation of 33 KV C.T.’s: Installation of 3 Nos. C.T.’s on the C.T’s structure. The work includes fabrication for proper fixing, if required to complete the work. | item44 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
45 | 33 KV CT’s Junction Box: Providing & fixing of junction box of size (400x400x150) mm made of M.S. sheet of 16 SWG in between 33 KV CT’s & control panel. The work also include making proper connection on the junction box and making all connection in between CT’s and control panel complete as per manufacture’s panel drawing including testing and commissioning of work etc. complete the work. | item45 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
46 | Installation of 33 KV Fuse Set: Assembling and installation of fuse set on the fuse set structure. The work includes fabrication for proper fixing, if required. | item46 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
47 | 33 KV Bus Bar Jumpering: Jumpering, including clamping/binding with ACSR Panther conductor/33KV 3x300mm2 XLPE cable with providing P.G.Clamp & other accessories. 33 KV Bus Bar to 33 KV P.I | item47 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
48 | 33 KV Post insulator to Bus isolator. | item48 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
49 | 33KV Bus isolator to 33KV VCB | item49 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
50 | 33KV VCB to 33KV CT | item50 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
51 | 33KV C.T to 33KV Fuse set. | item51 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
52 | 33KV Fuse set to LA | item52 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
53 | 33KV LA to 33/11KV 5/10MVA T/F | item53 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
54 | Testing & commissioning (To provide required No. of technicians to work on power T/f, HT/LT panels & 33KV line during testing as assisting technical hands of test team during commissioning & energisation). | item54 | 4 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
55 | Hiring of D/G Set including carriage, loading, unloading & operating charges (With fuel) at 33/11KV Substation under construction in case L.T. Supply is not available near S/s within prescribed accessible limit. 63KVA, Three phase, D/G Set for fabrication of different structure at Substation. | item55 | 4 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
Total in Figures | [51 empty] | 0 | 0 |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [7 empty] | % | [39 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information