## BoQ1 (hidden)
Item Wise BoQ
BoQ_Ver3.0 | Item Wise | Normal | INR Only | INR
Select, Excess (+), Less (-)
Tender Inviting Authority: Executive Engineer, Electricity Construction & Works Division, Ghaziabad | [54 empty] | Bought Out
Name of Work:-Works at proposed (1) Increasing capacity of 33/11KV Substation Balram Nagar, Loni, Ghaziabad (2x5)MVA to (5+10)MVA (2) Increasing capacity of 33/11KV Substation Ram Park, Loni, Ghaziabad (5+10)MVA to (2x10)MVA (3) Increasing capacity of 33/11KV Substation Maharajpur-II, Ghaziabad (2x10)MVA to (2x10+5)MVA | [54 empty] | Direct
Tender Reference No : 110/ECWD/Gzb/2023-24 | [54 empty] | Quote for Supply Portion only
Bidder Name : | [54 empty] | Quote for Erection Portion only
PRICE BID 1. This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns after validating the sheet, else the bidder is liable to be rejected for this tender. 2. Bidders are allowed to enter the Bidder Name and Unit Ex-Works Price and GST in %age only. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents. 9. BIDDERS MUST FILLED UP THE GST IN %AGE OTHERWISE G.S.T. RATES WILL BE TREATED AS INCLUDED IN THE GIVEN BASIC RATES.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Description of Works | Item Code | Tendered Quantity | Unit | Estimated Rate | Bought-out /Direct | Specify Bought-out /Direct | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Ex-Works Price (Rs./Unit) | Excise Duty (Rs/Unit) | CST/VAT (Rs/Unit) | Other Taxes & Duties (Rs/Unit) | Freight & Insurance Charges (in Rs./Unit) |  |  | Unit FOR Dest. Supply Price incl. all Taxes and Duties (in Rs./Unit) (F+G+H+I+J) | Total Value for work (In Rs.) (C x F) | GST (in %age) | Total Value for GST (in Rs.) |  |  | Total Unit Price incl. GST (in Rs.) | [26 empty] | Total Amount excl. GST (in Rs.) | Total Amount incl. GST (in Rs.) | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Carriage of following material from PVVNL Store 33KV Lightening arrester | item1 | 7 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [8 empty] | 18 |  | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2 | 33KV Bus isolator 800A, | item2 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
3 | 33KV Post insulator | item3 | 9 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
4 | 90 lbs rail pieces for T/F (44.64Kg/Mtrs.) | item4 | 7 | Mtrs | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
5 | 33KV VCB 1250Amp. | item5 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
6 | 33KV CT 200/100/1-1-1A | item6 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
7 | 33KV Control Panel for single Transformer | item7 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
8 | 11KV VCB for I/C CTR 600/300/5A, 350MVA | item8 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
9 | 11KV Outgoing CTR 200/100/5A 350 MVA | item9 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
10 | 11KV XLPE cable 3x300mm² | item10 | 205 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
11 | 11KV XLPE cable 3x185mm² | item11 | 60 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
12 | 11KV Cable J/kit outdoor type for 3x300mm / 3x185mm | item12 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
13 | 11KV Cable J/kit indoor type for 3x300mm / 3x185mm | item13 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
14 | Cable H.T.XLPE 33KV 3x300SQ.M.M | item14 | 100 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
15 | Cable Box O/D 33KV 3x300 XLPE | item15 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
16 | ACSR Dog Conductor | item16 | 150 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
17 | Transformer oil Fresh | item17 | 418 | Ltr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
18 | 11Mtr,STP-SP-55 Pole | item18 | 2 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
19 | Disc insulator Polymeric type 70KN | item19 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
20 | Disc fitting B&S type 70KN | item20 | 3 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
21 | 11KV composite Polymeric Pin insulator. | item21 | 6 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
22 | 11KV Fuse Set | item22 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
23 | 11KV TPMO | item23 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
24 | 11 KV Lightning arrestor | item24 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
25 | 33KV Fuse set | item25 | 5 | set | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
26 | Loading, Safe carriage & unloading of following stock material from any stores centres under PVVNL, depending upon the availability of material at Stores Centres, with loading & unloading at both ends respectively. Steel, 3.5Mtr long Rail Pieces, Angle channel, Conductor, M.S.Round etc. | item26 | 3 | MT. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
27 | Draining of oil from conservator & radiators of the 5MVA T/F, already available at any 33/11KV S/S / Store Centre of PVVNL into the dry & clean drums and staking at the safe place. | item27 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
28 | Dismantling of conservator, radiators and other accessories from above 5MVA Transformer at any 33/11KV S/S / Store Centre under PVVNL | item28 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
29 | Shifting of 05MVA T/F main body and other accessories from the Substation switchyard to loading point out side the switchyard of any 33/11KV Substation / Store Centre under PVVNL. | item29 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
30 | Loading of main tank of Transformer alongwith conservator, radiators, Transformer’s Oil Drums, and other accessories on the Trailer/Truck at any 33/11KV S/S / Store Centre under PVVNL | item30 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
31 | Carriage of main tank of Transformer alongwith conservator, radiators, Transformer’s Oil Drums and other accessories from any 33/11KV S/S of PVVNL to desired 33/11KV S/S. | item31 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
32 | Unloading of main tank of Transformer alongwith conservator, radiators, Transformer’s Oil Drums, and other accessories on the Trailer/Truck at 33/11KV S/S / Store Centre under PVVNL | item32 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
33 | Erection of following Material & Miscellaneous Electrical Works. LINE/BUS ISOLATOR STRUCTURE: (i) Fabrication and erection of Isolator structure (Bus / Line) each by using 3.5 m long 04 Nos. of M.S.Channel of size (125×65×6)mm with bracing by M.S.Angle (50×50×6)mm size and 02 Nos. M.S.Angle (75×75×8)mm of size and 2.6m long on the top of Channel at both side of Isolator. The work also includes cutting, drilling, welding and proper alignment of the same for completion of work. | item33 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
34 | Excavation of earth-2x(1.10x0.60x1.0)x1 | item34 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
35 | Erection of Line/Bus Isolator structure in proper alighment. | item35 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
36 | Grouting of structure in C.C. ratio 1:3:6 in size 2x(1.10x0.60x1.00)x1 All civil material supply by the Contractor | item36 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
37 | Making plinth by C.C. ratio 1:3:6, in size 2x(1.10x0.60x0.30)x1 All civil material supply by the Contractor | item37 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
38 | 12mm thick plastering on plinth in ratio 1:4 of size- 4x(1.10x0.30)x1+4x(0.60x0.30)x1+2x(1.10x0.60)x1 All civil material supply by the Contractor | item38 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
39 | Supply & fixing of stone pad. | item39 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
40 | L.A.’s, Fuse Set & CT,s (04 Nos.) structure:- Fabrication and erection of structure by using M.S.Channel (125×65) mm /(100×50) mm size and 3.5 m minimum height with 2 Nos. M.S.Angle (65×65×6)mm size on top of structure for installation. The work also includes cutting, drilling, welding and proper alignment of the same for completion of work. | item40 | 6 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
41 | Excavation of earth in size- 3x(0.45x0.45x1.00) | item41 | 6 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
42 | Erection of above structure. | item42 | 6 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
43 | Grouting by C.C. in ratio 1:3:6, (Cement, Course sand, stone grift). 3x(0.45x0.45x1.00) providing all requred civil material. | item43 | 6 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
44 | Making plinth by C.C. ratio 1:3:6, (Cement, Course sand, stone grift).3x(0.45x0.45x0.3) providing all requred civil material. | item44 | 6 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
45 | 12mm thick plastering on plinth in ratio 1:4 on plinth. | item45 | 6 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
46 | Supply & fixing of stone pad. | item46 | 12 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
47 | Plinth for 05 MVA Transformer Construction of plinth for 05 MVA, 33/11 KV Transformer of (3.46x3.46x1.0)m (0.50m below ground level and 0.5 m above ground level) as per details & drawing attached (All required matrials provided/Supply by the contractor own his cost):- Excavation of earth (3.7x4.7x0.5)m | item47 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
48 | Flooring of plinth in C.C. 1:4:8 (cement, sand & brick ballast) for making foundation bed. Size (3.7x4.7x0.15)m. | item48 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
49 | 1st Class brick work for side walls size 0.345 m wide upto 0.3m height and 0.23 m wide upto 0.35 m height cm C.C. ratio of 1:4 (cement & fine sand) | item49 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
50 | Filling of brick ballast in plinth in ratio 1:4:8 (cement, coarse sand & brick ballast) with proper ramming. Size (4.0x3.0x0.65)m. | item50 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
51 | R.C.C. work on the top of plinth in ratio 1:2:4 in (4.46x3.46)m size and 0.20m in thickness by using G.I. Tor of 12 mm dia. The work also includes cutting, bending of G.I. Tor etc. | item51 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
52 | Quantity of M.S. Tor of size 12 mm dia required for reinforcement of plinth in R.C.C. work for making jal in two layers. Work also includes cutting, bending and laying etc. in the T/F plinth. | item52 | 240 | Kgs. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
53 | Grouting of 02 Nos. 90/105 lb. Rail pieces of 3.46m long and (50x50x6)mm G.I. Angle in R.C.C. work at the top of plinth work also includes cutting of rail and angles pieces etc. | item53 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
54 | 12mm thick plaster with cement mortar ratio 1:4 (cement & fine sand) of plinth of 0.5m upper side (Top & side walls). | item54 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
55 | Removal of existing 5MVA Transformer and other accessories equipments. Disconnecting HT cable connection from 33KV side & 11KV side of 05MVA Power transformer for removing power transformer from plinth after proper shutdown. Dismantling of 11KV cable support structure, copper bus bar structure, M.S.Frame etc. | item55 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
56 | Disconnecting copper flexible/Earthing strip from Power transformer neutral & Dismantling neutral earthing system to facilitate removal of Power transformer from plinth. | item56 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
57 | Disconnecting Earthing strip from body of 05MVA Power transformer. | item57 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
58 | Draining of transformer oil from conservator, radiators of existing 05 MVA T/F, at 33/11 KV S/S into the dry & clean drums and stacking at the safe place in Substation outside of switchyard. Empty drums shall be provided by contractor | item58 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
59 | Removal of conservator, radiators and other accessories from existing 05 MVA Power transformer. | item59 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
60 | Safe Shifting of 05 MVA Power transformer main body and other accessories from the substation switchyard to outside the switchyard at suitable place assigned by concern J.E/S.D.O (Distribution). | item60 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
61 | Re-assembling of conservator, radiators and other accessories to existing 05 MVA Power transformer. | item61 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
62 | Re-filling the transformer oil (old & used in existing 5MVA T/F) | item62 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
63 | Installation for 33/11KV 10MVA T/F Safe Shifting of 10MVA, 33/11 KV, Power transformer from out side of switchyard to near Power transformer plinth in Switchyard. | item63 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
64 | Erection & Installation of 10MVA Power transformer on Power Transformer plinth by fixing all accessories like radiators, conservator tank, filling the transformer oil to desired level and ensuring that there is no leakage, complete job in all respect. Reconnecting 2 Nos. earthing strip to transformer body. | item64 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
65 | Installation for 33/11KV 5MVA T/F Safe Shifting of 05MVA, 33/11 KV, Power transformer from out side of switchyard to near Power transformer plinth in Switchyard. | item65 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
66 | Erection & Installation of 05MVA Power transformer on Power Transformer plinth by fixing all accessories like radiators, conservator tank, filling the transformer oil to desired level and ensuring that there is no leakage, complete job in all respect. Reconnecting 2 Nos. earthing strip to transformer body. | item66 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
67 | Plinth for 33 KV V.C.B. Construction of plinth for the structure of 33 KV VCB & C.T.’s as per details for 01 No. (All required materials provided / Supply by the contractor own his cost) :- Excavation of earth of size 2x(2.0x2.0x0.1)m pits for construction of plinth. | item67 | 4 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
68 | Brick Ballast ratio (1:4:8) (cement, sand & brick ballast) for foundation work 2x(2.0x2.0x0.5)m plinth. All civil material supply by the Contractor. | item68 | 0.6 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
69 | R.C.C. work in ratio 1:2:4 (cement, coarse sand & stone grit) of 20m size for making plinth of size 2x(2.0x2.0x1.0)m and grouting of foundation bolts 04 Nos. for 33 KV VCB. All civil material supply by the contractor. | item69 | 4 | Cum | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
70 | 12mm thick plaster with cement mortar in ratio 1:4 (cement & fine sand) of plinth. All civil material supply by the contractor. | item70 | 1 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
71 | Earth Mat Work Excavation of earth of size (0.5x0.75)m in switchyard area as per drawing for laying of 32 mm dia M.S. Round and 50x6mm size G.I. strip and refilling & ramming of the same earth into the trenches after completion of work. | item71 | 77 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
72 | Laying of 32 mm dia M.S. Round Bar in 0.75m deep trenches as excavated in items. 1(a) | item72 | 77 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
73 | Welding with lap joint minimum length 150mm over lapping on both side of item 1(b) (i) shall be done so that all the edges may fill completely with high quality Arc welding. All joints shall be painted with black bituminous paint. | item73 | 15 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
74 | Jointing of 32mm dia M.S. Round in earth mat at cross joint using high quality Arc welding 75mm piece of 32 mm dia M.S. Round shall also be welded to make the joints strong for transfer the fault current. Work also included cutting welding and painting with black bituminous paint of joint etc. | item74 | 15 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
75 | Fabrication of 32mm dia for 3.0 m long electrodes and driving them into ground so that the top of M.S. Round/Electrode remains at least 0.75 m below the ground level and jointing of earth electrode with the Earth Mat by using 75mm long piece of M.S.Round using high quality Arc welding and paints of joints with black bituminous paint. | item75 | 15 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
76 | Providing & Laying of G.I. Earth strip of size 50x6mm for earthing of new indoor equipments by connecting it existing indoor earthing. | item76 | 20 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
77 | Providing & Laying of G.I. Earth strip of size 50x6mm for connecting the Earth Mat with steel structure & chain link fencing’s posts. The work also includes cutting, bending, traight-tening, over-lapping and welding the Earth Strip with Earth Mat and various steel structures by using high quality Arc welding in already digged trenches. | item77 | 130 | Mt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
78 | Painting of Earth Strip of size (50x6) mm with one coat of ready mixed primer with two coats of ISI mark synthetic channel green paint. | item78 | 150 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
79 | Earthing of L.A's & Transforer neutral : Making of delta with 03 No. 03mtr. 32mm dia M.S. round bar electrode and Fabrication of 32 mm dia bar for 3.0 m long electrodes and digging them into ground so that the top of M.S. Round/Electrode remains at least 0.75m in air and jointing of earth electrode with the delta by using 75mm long piece of M.S. Round using high quality Arc welding and paints of joints with black bituminious paint. | item79 | 3 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
80 | Water level earthing by Boring and lowering of M.S. pipe size 40 mm dia & thickness 3mm into the ground at 50 Mtr depth or upto the water level with the lower end of solid copper cone Approx 225 mm long and 750 gm in weight shall be provided and screwed in pipe as well as bringing out a continuous copper wire 6 SWG from the cone up to the ground surface where it will be bolted to the M.S. earth Strip for Transformer neutral connection, the M.S.Earth strip size 50x6mm will be welded to the M.S. pipe and neutral earthing support & other installed equipment in switchyard. All required material provided / supply by the contractor own his cost. | item80 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
81 | Supply & Erection solid copper cone Approx 225 mm long and 750 gm in weight | item81 | 5 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
82 | CONSTRUCTION OF CONTROL CABLE TRENCH IN SWITCHYARD, AS PER DETAILS Excavation of earth in size 0.750x0.40m. | item82 | 10 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
83 | C.C.work in foundation in ratio 1:3:6 (Cement, sand & Brick Ballast) with proper ramming in size 0.750x0.15m. All civil material supply by the contractor. | item83 | 10 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
84 | Ist Class Brick work in cement mortar in ratio 1:3 in size 0.23x0.35m. All civil material supply by the contractor. | item84 | 10 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
85 | 25mm thick C.C. in floor of Cable Trench in ratio 1:2:4 (Cement, coursend and Stone grift) 20mm guage in size 0.3m width. All civil material supply by the contractor. | item85 | 10 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
86 | Providing & Grouting of M.S.Strip of size 450x25x6mm in cable trench 100mm above floor level and at equal space distance 300mm | item86 | 30 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
87 | Grouting of M.S.Angle Iron of size 50x50x6mm in upper edge of trench. | item87 | 20 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
88 | C.C.work on the Top in the ratio 1:2:4 in the grouting of Edge of the Trenches. 2x(20x0.23x0.06) Civil material supply by the Contractor | item88 | 10 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
89 | Plastering of Trench in Cement, Mortar in ratio 1:4, 12mm thick in cable trench. Civil material supply by the Contractor | item89 | 10 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
90 | Fabrication and fixing cable trench cover of M.S.Angle Iron size 50x50x6mm of size 0.3m wide 0.5 to 1.0 mtr length with proper welding of 8mm size of bar 2Nos. In length and 6Nos. in width. Work will be include providing of all required civil material & all fabrication material (M.S.Angle 50x50x6mm) 0.5 Mtr long | item90 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
91 | 1.00 Mtr long | item91 | 8 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
92 | Fabrication and erection of neutral earthing L Type support made of M.S. Channel size 100x50mm. Structure shall be 4 Mtr. Long with 1 Mtr. Arms. Structure shall be grouted in ratio 1:3:6 in block size 300x300x700mm and painted of welding joint with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint work includes connecting neutral bushing rod of power Transformer and M.S. Earthing strip with the help of flexible copper bond, M.S. Bolt and washer. | item92 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
93 | Fabrication and erection of cable support made of two pieces of M.S. Angle (65x65x6)mm, 2.75 meter long, joined to each other by means of 5 Nos. M.S. Flat (50x6) mm pieces of size 750 mm long each by welding at equal intervals and grouting in a block of size (300x300x700)mm in C.C. 1:3:6 (cement, coarse sand and stone ballast) complete and painted of welding joint with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint. Work includes providing of three Nos. M.S. clamps made of (50x6)mm M.S. Flat for holding the cable including nuts and bolts. | item93 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
94 | Fabrication and grouting of M.S. Frames 3.60 mt. long for support of copper Bus Bar. Bus Bar will be provided in L.V. side of Power transformer. The M.S. frame shall be made of M.S. channel (100x50)mm in ‘T’ shape. Providing 2 Nos. support of M.S. Angle iron (50x50x6)mm, 0.60mt. long below the top channel, drilling of 3 Nos. hole on the top channel for fixing of 11 KV pin insulator and painted of welding joint with one coat of Ready Mixed primer and Two coat of enamel Aluminium paint and grouting the frame in C.C. ratio 1:3:6 (cement, coarse sand and stone ballast) in a block of size (300x300x700) mm. The work also includes the fixing of 3 Nos. 11 KV pin insulator with pin and binding the copper Bus Bar with the pin insulator by Aluminium binding wire in complete. | item94 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
95 | Supply & Fabrication of copper bus bar of size (2500x50x6)mm in L.V. side of 10MVA 33/11 KV, power transformer, Work includes connection of outside bus bar in L.V. side busing rod of Power Transformer and other side with outdoor 11 KV cable box as well as providing empire tape and H.T. tape etc. for proper insulation work. | item95 | 9 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
96 | Installation of 11 KV Switchgears in Control Room Carefully & safely shifting of 11 KV switchgear panels from outside to inside the switch gear room grouting foundation of bolts in C.C. ratio of 1:2:4 (including cutting of RCC floor and finishing of RCC floor) as per requirement placing, aligning and fixing of 11 KV anchor GI bolts and nuts of proper size for completion of work in all respect. | item96 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
97 | Proper fixing and making bus bar connection in between two switch gears after proper cleaning. Work also include proper insulation, taping by empire, PVC and H.T. tape etc. | item97 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
98 | Earthing of 11 KV Switch Gears: Earthing of 11KV switchgears by means of M.S. earth strips (50x6) mm connecting to 4 Nos. earthing electrodes of 32 mm dia. (including fabrications of earthing electrodes) 3m long on either side (as per RESPO drg. RES-40). welding of M.S.Earth strips (50x6)mm and also laying of the M.S.Round 32mm dia in trench of control room and connecting to both sides squares including cost of M.S. earth strip (50x6)mm approx. 40m length and earthing of all indoor equipment by laying and providing M.S.earth strip (50x6)mm including cutting & welding etc. | item98 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
99 | H.T. Power Cable Laying: Laying 11 KV, (3x300) mm2 XLPE, Cable from power transformer to 11 KV incoming switch gear in the cable trench 0.50 m wide, 0.90m depth. Providing 150 mm local sand for cushion beneath and 150 mm above the cable (quality of local sand required 0.375 cum/m in length). The cable shall be dully protected by brick. On both side of cable by laying brick vertically and bricks would also be laid bricks along the single cable (minimum 18 Nos. of bricks are to be laid top and outer side along the single cable. The work includes digging of trenches, laying of cable in under ground trenches, joining of terminal’s, back filling of earth and testing and commissioning of power cable etc. Spare cable shall be left over and laid in the trenches in shape of 6 m ring at both ends. | item99 | 160 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
100 | Laying and dressing of 11 KV 3x300 mm2 power cable in air/Trench. | item100 | 45 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
101 | Laying 11 KV, 3x185mm2 XLPE, Power cable from outgoing switch gear to 11 KV double poles in the cable trench 0.50m wide, 0.90m depth. Providing 150 thickness mm local sand for cushion beneath and 150mm above the cable (quantity of local sand required 0.375 cubm/m in length). The cable shall be duly protected by brick. On both side of cable by laying bricks vertically and bricks would also be laid horizontally on top of vertically laid bricks along the single cable (minimum 18 Nos. of bricks are to be laid top and outer side along the single cable. The work includes digging of trenches, laying of cable in under ground trenches, joining of terminal’s, back filling of earth and testing and commissioning of power cables etc. Spare cable shall be left over and laid in the trenches in shape of 6m rings at both ends. At the end of feeder cables, where the cable is to be laid across pucca/main road, 100 mm dia M.S. pipe will be weared over the cable in the cable trench for the protection of cable. | item101 | 40 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
102 | Laying and Dressing of 11KV 3x185mm² Power Cable in Air. | item102 | 20 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
103 | Preparation of 11 KV Power Cable ends: Making of 11 KV XLPE Heat shrinkable outdoor jointing kits 3x185Sq.mm/3x300Sq.mm after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs | item103 | 5 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
104 | Making of 11 KV XLPE heat shrinkable indoor jointing kits 3x185Sq.mm/3x300Sq.mm in switch gears after carefully removing the insulation of cable, providing and crimping of proper size of lugs, plumbing and taping of cable with good quality available insulation tape with J/Kit boxes, Fixing and insulating of lugs on cable with switch gear complete in all respect. | item104 | 5 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
105 | Supply & Laying of different size of (2x2.5)mm2 control cables i.e. from Buchholz realy to Marshalling box Marshalling box to indication protection board in switch gear room, 33 KV CT’s to CT’s Junction Box, 33 KV CT, 33 KV PT, V.C.B. Control Panel Junction Box to 33 KV VCB control panel and control panel to 33 KV VCB outdoor operating mechanism panel from T/F etc. in the cable trench including making proper connection at Buchholz Relay, Marshalling box and indication board as per required for installed equipment. | item105 | 250 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
106 | Supply & Laying of different size of (4x2.5)mm2 control cables i.e. from Buchholz realy to Marshalling box Marshalling box to indication protection board in switch gear room, 33 KV CT’s to CT’s Junction Box, 33 KV CT, 33 KV PT, V.C.B. Control Panel Junction Box to 33 KV VCB control panel and control panel to 33 KV VCB outdoor operating mechanism panel from T/F etc. in the cable trench including making proper connection at Buchholz Relay, Marshalling box and indication board as per required for installed equipment. | item106 | 470 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
107 | Construction of 11 KV Feeder Double Poles: Erection and grouting of 2 Nos. STP-55-11Mtr long for making DP Structure including fabrication fixing of M.S. Channel, M.S.Angle, TPMO, Fuse Set, disc, insulators, pin insulators No. Plate, Danger board, barbed Wire (02 Kg per Pole) etc. the work includes supply and fixing of necessary clamps size 75x10mm with M.S.Nuts bolt & washer, bolts and washers. The work also includes grouting of Double pole support in C.C. 1:3:6 (cement, Core sand & stone ballast) in block of size (0.45m x 0.45 x 1/6 length of the pole) including earthing of Double pole with M.S. earthing rod complete in all respect. | item107 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
108 | Providing & wearing of 110 mm dia 3.0 mm long G.I.Pipe in the feeder cable of size of (3x185/3x300)mm2 XLPE 11KV power cable before making the outdoor cable boxes. The work includes the sealing of G.I.Pipe, top end and lower end of the pipe is to be buried in to the ground about ½ m and proper dressing of cable etc. The work includes lifting, mounting and clamping of 11 KV feeder cable boxes on the feeder with double pole structure and making connections including supply of cable mounting clamps etc. | item108 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
109 | Painting of Structures Painting of the following structure with one coat of ready mixed primer and two coats of ISI Mark Aluminium paint after rubbing with sand paper to the surface of the structure including labour and T&P complete in all respect. Painting of Substation Structures | item109 | 3 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
110 | Installation of 33 KV Isolators: Assembling and installation of line/Bus Isolator on the isolator structure. Adjusting of operating mechanism in proper alignment so as to ensure smooth operation of the same. In case of Line Isolator proper operation of earth links shall also be ensured. The work includes fabrication for proper fixing if required. | item110 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
111 | Installation of 33 KV Lightning Arrestors: Assembling and installation/mounting of 3 Nos. lighting arrestors on the L.A.’s structure/terminal gentry, complete with earthing and line connections. The work includes fabrication for proper fixing, if required. | item111 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
112 | Installation of 33 KV Post Insulators: Installation of 3 Nos. PI on structure. The work includes fabrication for proper fixing, if required. | item112 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
113 | Installation of 33 KV VCB Assembling and installation of 33 KV VCB on the VCB out door structure on the plinth. Adjustment of operating mechanism in proper alignment for smooth operation of the same. The work also includes fabrication of addition arrangement for proper fixing, if required. | item113 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
114 | Installation of 33 KV VCB Control Panel for Double T/F Carefully and safely shifting of 33 KV VCB control panel from outside of the switch gear room to inside of the switch gear room, grouting with anchor bolts in the floor, work also includes cutting & proper finishing of floor if necessary for completion of work. Placing and fixing of panel on foundation, bolts of proper size in proper position and alignment. | item114 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
115 | Installation of 33 KV C.T.’s: Installation of 3 Nos. C.T.’s on the C.T’s structure. The work includes fabrication for proper fixing, if required to complete the work. | item115 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
116 | 33 KV CT’s Junction Box: Providing & fixing of junction box of size (400x400x150) mm made of M.S. sheet of 16 SWG in between 33 KV CT’s & control panel. The work also include making proper connection on the junction box and making all connection in between CT’s and control panel complete as per manufacture’s panel drawing including testing and commissioning of work etc. complete the work. | item116 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
117 | Installation of 33 KV Fuse Set: Assembling and installation of fuse set on the fuse set structure. The work includes fabrication for proper fixing, if required. The work also includes removing of old / damaged fuse set if required. | item117 | 5 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
118 | 33 KV Bus Bar Jumpering: Jumpering, including clamping/binding with ACSR Panther conductor/33KV 3x300mm2 XLPE cable with providing P.G.Clamp & other accessories. 33 KV Bus Bar to 33 KV P.I | item118 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
119 | 33 KV Post insulator to Bus isolator. | item119 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
120 | 33KV Bus isolator to 33KV VCB | item120 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
121 | 33KV VCB to 33KV CT | item121 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
122 | 33KV C.T to 33KV Fuse set. | item122 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
123 | 33KV Fuse set to LA | item123 | 2 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
124 | 33KV LA to 33/11KV 5/10MVA T/F | item124 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
125 | Digging of Trench by excavation of earth of 1050x750mm size for 33KV line | item125 | 30 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
126 | Safe laying of 33KV, 3x300Sq.mm. XLPE Cable in Cable Trench to respective Double Pole. | item126 | 60 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
127 | Providing & Laying of Ist Class Bricks, along the length on both side of 33KV XLPE Cable in Cable Trench (minium 18No. Bricks/Mtr per Cable) and Stone Slab (Smooth surface both side) of size 400x600x40mm on top of the Cable, Providing 75mm thickness River sand for cushion beneath and 75mm above the cable as per specification. | item127 | 30 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
128 | Back filling of excavated earth in the cable trench upto the ground level and ramming properly. | item128 | 30 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
129 | Laying of 33KV, 3x300Sq.mm XLPE Cable in the air / Pucca trench on cable Riser Double Pole, existing cable trench, | item129 | 40 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
130 | Making of 33KV Outdoor type cable end termination by heat shrinkable XLPE Cable Jointing Kits and crimping with proper size aluminium lugs. Work includes providing Aluminum lugs, insulating tapes etc as per specifications. | item130 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
131 | Testing & commissioning (To provide required No. of technicians to work on power T/f, HT/LT panels & 33KV line during testing as assisting technical hands of test team during commissioning & energisation). | item131 | 3 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
132 | Construction of SSO’s approached road 1.2 Mt wide in switch yard by laying dry brick ballast in 15 cm layer, 115 mm thick brick work 1:4 in both side of edge, providing 10 cm thick CC in ratio 1:2:4. The work include proper plastering top & side of road and making groove, leveling & dressing of earth beneath the brick work on edge. All required materials provived / supply by the contractor own his cost. | item132 | 10 | RM | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
133 | Construction of control Room trench as per PVVNL Specification. | item133 | 6 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
134 | Construction of fire protection wall size 5Mtrx4.5Mtr above ground level (as per approved Drawing). Providing required Civil Material by the Contractor. | item134 | 1 | Job | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
135 | Hiring of D/G Set including carriage, loading, unloading & operating charges (With fuel) at 33/11KV Substation under construction in case L.T. Supply is not available near S/s within prescribed accessible limit. 63KVA, Three phase, D/G Set for fabrication of different structure at Substation. | item135 | 3 | Job. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
Total in Figures | [51 empty] | 0 | 0 |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [7 empty] | % | [39 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information