Tender specification no. PVVNL-MT/COM/33(s)/21-22

TECHNICAL SPECIFICATION FOR 11 KV CT

1.0	GENERAL:

  - This specification covers the design, manufacture testing and supply of 11 KV CT.

  - The CT shall comply with the requirements of the relevant I.S. specifications.

  - List of raw material to be along with the name of suppliers should be submitted with the 	tender.

2.0	ELECTRICAL COMPONENTS:

The supplier shall be original manufacturer of the epoxy resin cast CT or accredited representative of such manufacturer. The bidder must have facility to cast epoxy resin by hot casting process under vacuum for CTs at his own works. These CT should have been type tested  as mentioned elsewhere in the tender specification as per relevant ISS (latest revision) in a Govt. accredited National Test House such as CPRI, Bangalore / Bhopal etc during the last five years from the date of Tender opening.

3.0	MAIN PARTICULARS OF CURRENT TRANSFORMERS:

Single Core single ratio dry type epoxy resin cast type current transformers as per IS: 2705: 1992 of latest revisions thereof as per details mentioned below: -

| S.No. | ##### TYPE |  | Dry type epoxy Resin cast type CTs. |
| --- | --- | --- | --- |
| 1 | ##### Ratios |  | 5/5A,10/5A,15/5A,20/5A,25/5A,30/5A,40/5A, 50/5A,60/5A,75/5A,80/5A,100/5A,125/5A,150/5A 200/5A or higher ratio |
| 2. | Nominal system voltage (KV rms.) | : | 11 |
| 3. | Highest system voltage (KV rms.) | : | 12 |
| 4. | Frequency | : | 50 Hz. |
| 5. | Rated output (V.A burden) | : | 10 VA |
| 6. | Current density at rated current(Max) | : | 1.5 Amp. Per sq. mm |
| 7. | Current density at STC for 1 second(max) | : | 165 Amp. Per sq. mm |
| 8. | Cross sectional area of primary As per current density | : | Should be as per rated current density or as per current density at STC (for 1 second) whichever is higher |
| 9. | Class of accuracy | : | 0.5 S |
| 10. | Rated continuous thermal current | : | 1.2 times of rated primary current. |
| 11. | Short time thermal current rating | : | 5/5: 3 KA for 0.5 sec. 10/5-20/5: 3 KA for 1.0 sec. 25/5-40/5: 7.8KA for 1.0 sec. 50/5-100/5: 13 KA for 1 sec 100/5-250/5 : 18 KA for 1.0 sec etc as per relevant IS |
| 12. | Rated dynamic current rating | : | 2.5 times of short time thermal current rating |
| 13. | Instrument Security factor | : | < 5 |
| 14. | All other characteristics and test parameter | : | As per IS: 2705/1992 (latest version) |
| 15. | Max temperature rise over ambient temp of 50º at rated continuous thermal current at rated frequency rated bush. | : | 45ºc |

#### Material

(i)	Core	High-grade non-ageing electrical low loss core of superior CRGO silicon sheet steel.

(ii)	Conductor			Super enameled copper wire

(iii)	Insulation			Resin cast.

(iv)	Base 				MS Hot dip galvanized.

- Primary termination 		Tinned Copper strips with sleeves 50x6 mm size as      				per relevant ISS, with clear polarity making P1&P2.

The strips should be suitably so bended as to 	facilitate smooth jointing with 11KV incoming and 	outgoing cable lugs.

(vi)	Secondary Termination	Firm and effective Termination with clearly polarity 				marking s1 & s2

The current transformer should be type tested and routine tested as per IS: 2705:1992 or latest amendment thereof.

4.0	MAKE OF THE COMPONENT:

List of raw material to be used along with names of the suppliers should be submitted 	with Part-I of the tender. Make of various components as detailed above and as being 	given below.

4.1	HARDWARE:

Hot-Dip Galvanized of any standard make.

4.2	PAINT:

Epoxy – Paint of standard make.

  - EPOXY RESIN :–

Dr. Beck, Huntsman, Atul.

5.0	INSPECTION AND TESTING:

CTs shall be inspected and tested at manufacturer works to verify that these are being supplied in accordance with relevant standards. Technical Specification, Guaranteed Technical Particulars and acceptance and routine tests.

Inspection of material offered for inspection shall be carried out by the representatives of Superintending Engineer (Quality Cell), PVVNL, Meerut.

While offering for inspection /testing confirmation to the effect that the cubicle have successfully withstood the routing tests (along with test results)  is required to be submitted for each lot offered for inspection Superintending Engineer (Quality Cell), PVVNL, Meerut.

All testing equipment used in inspection and testing should be properly calibrated and sealed once a year. Calibration certificate when demanded by the inspecting officer shall be provided / produced for verification purpose. In case of any dispute regarding calibration, instruments shall be sealed and singed by the representative of the supplier and purchaser and will be sent to test house / Govt. Lab / Govt. institution of repute, for calibration at the cost of supplier. The result of such testing shall be binding on the supplier.

Purchaser reserves the right to get the CT's inspected / type tested before dispatch by any independent inspection agency at the cost of purchaser in case the equipment with stand the type test, otherwise the supplier has to bear such cost in addition to any other action deemed appropriate by the purchaser.

One sample of CT of any ratio randomly selected from each offered lot, shall be opened for verifying the diameter & cross sectional area of primary coil conductors including verification of GTP

Testing Facility: - The manufacturer must have testing facilities at their works as per clause No. 1.2.3 of "Instruction to Tenderer" to carry out all the routine & acceptance test (including partial discharge test) as mentioned below. List of Testing equipment with photo copy of calibration certificates should be enclosed with Part- I & II of the tender.

5.1	Type test:

All the type tests as listed below shall be carried out for the equipment strictly as described as per the relevant IS (or latest amendment thereafter).

Current Transformers (As per IS: 2705 / 1992 or its latest Amendment)

(A) Type Testing will be done on CT of any one ratio if-

(i)	The type tested CT has maximum dynamic AT’s in confirmation to IS: 2705,       1992 Clause no. 9.6.2 (Notes)

(ii)	The shape size construction of all the ratio is same.

However if shape size & construction varies for different ratio’s then all type test shall be repeated accordingly for each shape, size & construction.

a)	Short-time current test.

b)	High Voltage power frequency on primary windings.

c)	High Voltage power frequency on secondary windings.

d) 	Lightning impulse test

e)	Determination of error according to the requirements of appropriate accuracy class

f)	Temperature rise test on any one selected sample of each ratio.

g)	Partial discharge test

h)	Instruments security factor (ISF) test as per IS: 2705.  Part-II or any latest amendment.

5.2	Routine Tests: -

The following shall constitute the routine test and acceptance tests.

5.2.1 	Current Transformers

a)	Verification of terminal markings and polarity

b)	High Voltage power frequency test on primary windings.

c)	High voltage power frequency test on secondary windings.

d)	Over voltage inter turn test.

e)	Determination of error according to the requirements of appropriate accuracy class.

f)	Partial discharge test in accordance with IS: 11322 / 1985.

g)	Instruments security factor test(IFS) as per IS:2705.

5.3	Acceptance Test:

5.3.1 	Current Transformers

a)	Verification of terminal markings and polarity

b)	High Voltage power frequency on primary windings.

c)	High Voltage power frequency on secondary windings.

d)	Determination of error according to the requirements of appropriate accuracy class

e)	Temperature rise test on any one selected sample of each ratio.

f)	Partial discharge test

g)	Instruments security factor test (ISF) as per IS:2705, Part-II (7.1.2)

6.0	In case of any discrepancy between specification and relevant standard, provision contained in this specification shall prevail.