PVVNL-MT/COM/09(s)/23-24

TECHNICAL SPECIFICATION FOR A.C.THREE PHASE FOUR WIRE H.T. A.C. TRI VECTOR

METER OF ACCURACY CLASS-0.5S FOR 11KV -/5 AMP & 33KV -/1 AMP NET METERING

SYSTEM WITH DLMS AS PER IS:15959 FOR SOLAR APPLICATION

1.0	SCOPE:

This specification covers the manufacture, testing and supply of C.T. and P.T. operated H.T. Trivector Meters of accuracy class–0.5S with TOD (Time of Day) and R.T.O. (Real Time  Clock) provisions and  performing  functions  as tariff  meters  and for energy  audit and  load  survey  applications.  These  meters  shall  be  capable  of  measurement  and recording  of  Active  Energy  (K.W.H.),  Reactive  Energy  (KV  Arh)  and  apparent  Energy

(KV Ah) for balance/unbalanced load at all Power Factors i.e. Zero-lag-Unity – Zero lead for Net Metering (Solar Application).

2.0	STANDARD:

The meters with accuracy class–0.5S are required measurement of Active Energy and shall conform to the latest edition of following standards:—

IEC 62052-11	:	Electricity  metering  equipment  (AC)

–  General  requirements,  tests  and test conditions, Metering equipment

IEC 62053-22:	:	Static	meters	for	active	energy,

(classes 0.2 S and 0.5 S)

CBIP 325:	:	Standardization	of	AC	Static Electrical Energy Meters, publication no. 325

IS:14697:1999	read	with	latest revision thereof

:	Indian	Standard,	AC	Static Transformer Operated Watthour and Varhour  meters,  classes  0.2  S  and

0.5 S

IS 15959	:	Data  exchange  for  electricity  meter reading,   tariff   and   load   control   - Indian Companion Standard

Meters  meeting  other  authoritative  standards  which  ensure  an  equal  or  better  quality than the standard mentioned above, will also be acceptable. All kinds of tests which are required as per (IEC-687)/CBIP report No. 325 and latest amendment thereof  shall be carried out.

3.0	CLIMATIC CONDITIONS:

The  meter  shall  be  required  to  operate  satisfactorily  and  continuously  with  specified accuracy under hot, dusty and tropical conditions and other climatic condition specified as hereinafter:—

1

i)	Specified operating range	:	–10C to + 55C ii)	Limit range of operation	:	–20C to + 60C iii)	Limit range of storage and Transport	:	–25C to + 70C iv)	RECATIVE HUMIDITY:

(a)	Annual Mean	:	<75ñ

(b)	For 30 days (spread over one year)	:	<95ñ

(c)	Occasionally on other days	:	100ñ

v)	Maximum attitude above M.S.I.	:	1000 Meter vi)	Average Annual rain fall	:	1200 mm.

4.0	CURRENT AND VOLTAGE RATING:

The Rated Basic and maximum current of 11kV Static Trivector Meters shall be as given below :—

Sl. No.

Voltage	Basic current

Maximum current (A)

Rated Voltage

(Phase to

Neutral)

1	2	3	4	5

1.	11KV	5 Amp.	2 Times Ib	63.5 Volt

2.	33KV	1 Amp.	2 Times Ib	63.5 Volt

Above data indicate that max. current is 200% of Ib at which the meter purports to meet the accuracy requirement.

5.0	VARIATION IN POWER SUPPLY:

The  meters shall be  suitable for working  satisfactorily with  the following  power supply system variations:—

5.1	VOLTAGE RANGE:

(i)	Specified Operating Range	:	0.8 to 1.1 Vref.

(ii)	Limit Range of Operation	:	0.7 to 1.2 Vref i.e.

–30% to + 20%

The  meter  shall  be  able  to  perform  without  any  change  in  accuracy  class  within  the specified voltage range and shall also be within the limits as CBIP Report No. 325.

5.2	FREQUENCY VARIATION:

The standard reference frequency for performance shall be 50Hz with tolerance + 5%.

6.0	POWER CONSUMPTION:

2

6.1	VOLTAGE CIRCUIT:

The active, apparent Power consumption in each voltage circuit of a meter at reference voltage,	reference	temperature	and	reference	frequency	shall	not	exceed	1.0

Watt/phase and 4VA per phase. The above figures are mean values.

6.2	CURRENT CIRCUIT:

The apparent Power taken by each current circuit at basic current, reference frequency and reference temperature shall not exceed 1.0 VA per phase.

6.3	POWER FACTOR RANGE:

The meter shall be suitable for Power factor range Zero–lag–Unit–Zero–Lead.

Apparent Energy shall be computed considering reactive ( lag + lead )

i.e. Apparent Energy =√ [Active Import Energy]2  + [ Reactive Energy ( Lag + Lead) ]2

6.4	STARTING CURRENT:

The meter should start registering the energy at 0.1 percent of basic current.

6.5	ACCURACY:

Class of accuracy of meter shall be 0.5S and shall confirm to accuracy requirement as per specify IS/IEC.

7.0	MEASURING PARA METERS:

The  meter  shall  be  capable  of  measuring  accurately under  balanced  and  unbalanced conditions at all Power Factures:

(1)	The real time and date	:

(2)	Active Energy	:	KWH

(3)	Active Energy during specified T.O.D. hours.	:	KWH

(4)	Reactive Energy	:	KVARH

(5)	Apparent Energy	:	KVAH

(6)	Apparent	Energy	during	specified	T.O.D. hours

(7)	Max.  Demand  with  date  and  time  with  30

minutes integration period.

:	KVAH

:	KVA

(8)	Cumulative Max. Demand	:	KVA

(90)	Max. Demand reset count.	:	Nos.

(10)	Average P.F. for a specified period	:	P.F.

(11)	Frequency	:	Hz.

(12)	Tamper  and  fraud  details  such  as  type  of	:

tamper, and tamper-counts.

7.1	DISPLAY PARAMETERS & TYPE OF DISPLAY:

3

Meter shall be capable of displaying above parameters in the following sequence within specified limits of errors for balanced or unbalanced load at all P.F. as mentioned hereinafter:—

Push Button Mode Display Parameters:

	LCD Test

	Real Time

	Date

	R Phase Line current

	Y Phase Line current

	R Phase Line current

	Phase to Neutral voltage R

	Phase to Neutral voltage Y

	Phase to Neutral voltage B

	Instantaneous Average Power factor

	Frequency

	Instantaneous Active Power

	Instantaneous Reactive Power

	Instantaneous Apparent Power

	Cumulative Tamper Count

	Cumulative MD reset count

	Cumulative Active Net Energy

	Cumulative Active Energy (Import & Export)

	Cumulative reactive lag energy (Import & Export)

	Cumulative reactive lead energy (Import & Export)

	Cumulative apparent energy (Import & Export)

	Current active maximum demand with date & time (Import & Export)

	Current apparent maximum demand with date & time (Import & Export)

	Cumulative active maximum demand (Import & Export)

	Cumulative apparent maximum demand(Import & Export)

	Present PT Status

	Present CT Status

	Other Status

	Last occurrence Tamper ID

	Date of last occurrence Tamper

	Time of last occurrence Tamper

	Last Restoration tamper ID

	Date of last restoration Tamper

	Time of last restoration Tamper

Auto Mode Display Parameters:

4

1.	LCD

2.	Real Time

3.	Date

4.	Cumulative Active Net Energy	KWH

5.	Cumulative Active (Import & Export) Energy	KWH

6.	Cumulative  reactive  lag  (Import  &  Export)

energy

7.	Cumulative  reactive  lead  (Import &  Export)

energy

8.	Cumulative	apparent	(Import	&	Export)

energy

9.	Cumulative Active Energy of individual Time Zone during specified peak hours (Import & Export)

10.	Cumulative  Apparent  Energy  of  individual time   Zone  during   specified   T.O.D  hours

(Import & Export)

11.	Current  month  maximum  demand	(Import

& Export)

12.	Cumulative   maximum  demand   (Import  & Export)

KVARh Lag

KVARh Lead

KVAH

KWH

KVAH

KVA

KVA

13.	Maximum demand reset count	Nos

14.	Instantaneous average power factor

15.	Frequency	Hz

16.	Instantaneous voltage of all three phases	Volts.

17.	Instantaneous current of all three phases	Amps.

18.	Present PT Status

19.	Present CT Status

20.	Other Status

21.	Last occurrence Tamper ID

22.	Date of last occurrence Tamper

23.	Time of last occurrence Tamper

24.	Last Restoration tamper ID

25.	Date of last restoration Tamper

26.	Date of last restoration Tamper

27.	Cumulative Tamper Count

NOTE: - Unit of Energies & MD will depend upon commissioning.

Parameter value with relevant OBIS code should be made available on display.

Meter  should  be  supplied  with  Backlit  LCD  display  the  measured  value(s)  shall  be displayed   on   seven   segments,   seven   digit   liquid   crystal   Display   (LCD)   display unit/register having  minimum character height  of 8 mm.  The  data  should  be  stored  in non volatile memory and should retain data for a period of not less than 10 (Ten) years under un-powered condition. Battery backup memory will not be considered as NVM.

5

Meter  shall  have  feature  of  connection  check  i.e.  PT  missing,  CT  reversal  on  meter display itself. PT missing & CT reversal shall be checked from looking on meter display. Meter  shall  have  the  facility  to  lock  any  parameter  on  display  screen  i.e.  Scroll  lock facility.

The display of various parameters shall be continuously scrolling one after another. The display shall have  ON time of  at  least  10  seconds for each  measured  value for auto- display cycling. The meter should have facility for a manual mode where the parameters can be read by push-button mode should have priority over auto display.

The meter should have non-volatile memory, so that the registered parameters will not be affected by loss of power. The battery backup memory will not be considered as Non Volatile memory.

It  should  be  possible  to  easily  identify  the  single  or  multiple  displayed  parameters through symbols/legend on the meter display itself or through display annunciator.

The  register  shall  be  able  to  record  and  display  starting  from  zero,  for a  minimum  of

1500  hours,  the  energy corresponding  to  rated  maximum current at  reference  voltage and unity power factor. The register should not roll over in between this duration.

7.2	SPECIAL RECUIREMENT FOR DISPLAY:

7.2.1	The meter shall have indication for unsatisfactory/non-functioning of the following:—

a)   Time and calendar

b)   Real time clock with battery c)   All display segments

d)   Non-volatile memory.

7.2.2	The meter serial number, C.T. and P.T. ratio and date with time of taking reading shall invariable be available at base computer software.

7.2.3	The meter shall be factory programmed for each and every month for minimum 20 years at the time of  manufacture and correctness of  20 years calendar. In addition following parameters should also be factory programmed:—

a)   CT/PT Ratio

b)   Integration period c)   Display sequence

7.2.4	The meter shall have provision of reading in the absence of power through an external source.  An  inductive  coupling  arrangement  shall be  provided  so  that  it  should  not  be possible  to  damage  the  circuit  of  the  meter by applying  excess voltage  directly in  the meter. The meter should be powered up using an external battery pack only in absence

6

of  power  supply  to  the  meter  to  enable  taking  of  meter  reading  through  display  and optical communication port.

If any bidder proposes for Internal Battery backup in the meter in case of mains supply failure for meter reading and meter data downloading, no power shall be consumed for this circuit when mains are available to recharge the battery.

In case of power failure data downloading for Historical energy, maximum Demand & all the tamper events through CMRI (common meter reading instrument) shall be possible through battery internal/ external backup. Rechargeable battery backup power shall not be used for display under Power absence condition. To verify that the sample meters are not having rechargeable battery, the samples will be kept in power off conditions for 7 days (168Hrs.) and  then  meters will be  checked by pressing  the  push  button  and  the CMRI shall be done.

7.2.5	Meter  shall   invariably  be  provided   with  LCD  display  cycling  facility  for  essential parameters, as envisaged under clause No. 7.0 of the technical specification.

7.2.6	While installing the meter, it shall be possible to check the correctness of the C.T. & P.T. connections  to  the  meter  and  their  polarity  with  the  help  of  common  meter  reading instrument.

7.2.7	The meter and related instruments, when installed, shall be constructed in a way offering full  protection  against  contact  voltage,  other  hazards  resulting  from/or  related  to  the operating  principle  and  the  utilization  of  the  equipment.  In  particular  if  any  metal  part accessible while covers are in place, then the base shall be fitted with protective Earth terminal identified by the Earthing symbol  and connected to all accessible metal parts.

7.2.8	The Static Tri vector Meter shall measure and retain previous 12 months data  (month wise) of the KWH (Import & Export) and KVAH (Import & Export) reading at 2400 Hrs. of the  last  day  of  each  calendar  months,  Average  Power  Factor  and  maximum  demand

(Import  &  Export)  with  date  and  time  of  occurrence  of  that  particular  month  for  all specified time zones. These parameters shall also be obtainable through common meter reading instrument whenever required of last 12 months

7.2.9	The meter should remain powered up and functional even when either any two phases or any one phase with neutral is available to the meter.

7.2.10  The meter shall be provided with an accurate quartz crystal based real time clock. The maximum drift permissible in the real time clock shall be +5 minutes per year for class

0.5S Meters.

7.2.11  All the registers and other parameters shall be updated every second.

7.2.12  The meter should work accurately irrespective of phase sequence of the mains supply only in forward direction.

7

8.0	MAXIMUM DEMAND REGISTRATION AND RESETS:

8.1	The  meter  shall  continuously  monitor  and  calculate  the  average  maximum  demand

(Import & Export) for each interval of time of 30 minutes and maximum of these shall be stored alongwith date and time when it occurred.

8.2	The meter shall automatically store the 30 minute average demand. At the end of every

30  minutes,  the new calculated demand  should be  compared  with  previous maximum demand  and  stored  whichever  of  them  is  higher.  The  maximum  demand  for  every calendar month alongwith the date and time when it occurred should be registered.

8.3	The maximum demand shall automatically reset at 24.00 Hrs. or  the last date of each calendar  Month  for  which  minimum  30  calendar  years  shall  be  programmed  by  the manufacturer at his work.

8.4	The  meter shall be provided  with  its own  real time  clock calendar with built  in battery backup and time derived from this clock shall be used for maximum demand intervals.

8.5	The billing purpose parameters for both import and export mode (active energy, apparent energy, maximum demand in kW and kVA) shall be registered and shall be available for a minimum period of last 12 (Twelve) months through BCS. Midnight data (KWH, KVAH) of last two months shall be provided in MRI.

9.0	LOAD SURVEY CAPABILITIES:

The meter shall be capable of recoding following parameter for the least 35 days with 30

minute integration period –

	Active (Import & Export) (Kwh)

	Apparent (Import & Export) (KVah)

	Phase Voltage (V1, V2, V3)

	Phase Current (Ir,Iy,Ib)

9.1	The meter shall have test output device accessible from the front and capable of being read  with  suitable  testing  equipment.  The  output  device  may  be  either  in  the  form  of pulses or in the form of high resolution display.

9.2	The  meter  shall  be  capable  of  storing  KVA  demands  at  30  minutes  interval  for  a minimum of last 35 days. The maximum demand in last 12 months with date and time of occurrence and tamper details as per clause 15.0 in its non-volatile memory and it shall be possible to transfer this data via a galvanically isolated optical communications port on to a base computer station through a DOS based CMRI or remotely using the remote communication interface as and when desired. Load profiles can be viewed graphically/ analytically  with  the  help  of  meter  application  software.  The  offered  meter  application software shall be capable of exporting these data for analysis to other user software in spreadsheet format (XML/Excel etc.).

9.3	The operational indicator if fitted, must be visible from the front.

10.0	TIME OF DAY (TOD) TARRIF:

10.1	Meter  should  be  able  to  store  apparent  and  active  energies  consumption  alongwith maximum demand in KVA for atleast different 8 time Zones.

8

10.2	Meter shall be able to record and store apparent and active energies, consumption alongwith maximum demand in KVA during specific peak hours described as following time Zone of register in sequence:—

- 17.00 to 18.00 Hrs.

- 18.00 to 22.00 Hrs.

- 22.00 to 23.00 Hrs.

- 23.00 to 05.00 Hrs.

- 05.00 to 06.00 Hrs.

- 06.00 to 08.00 Hrs.

- 08.00 to 11.00 Hrs.

- 11.00 to 17.00 Hrs.

10.3	The TOD zones should be available on display for information purpose.

10.4	The  meter  shall  have  facility  for  recording  and  storing  of  TOD  consumption  and maximum demand data on minimum Three Tariff Rates, per day basic.

10.5	It should be possible to change the time period for TOD recordings through the portable device  or  programmable  BLOCK  installed  in  the  meter  it  self  or  manually  with  proper security. The main control for this change shall be available on the computer located at the Metering Office.

11.0	COMMUNICATION CAPABILITY:

The meter shall have facilities for data transfer locally through CMRI with proper security via  an  optically  isolated  communication  port  using  serial  communication.  It  should  be possible  to  configure  meter for TOD tariff  demand  integration  period,  billing date,  real time clock and date etc. through CMRI locally without any extra cost to PVVNL, but the same  shall  be  done  by  us  only  after  taking  due  approval  of  MD,  PVVNL  or  his authorized   representative.   The   meters   shall   have   a   galvanically   isolated   optical communication ports as per IEC 1107 so that it can be easily reading instrument for data transfer. The meter shall have additional RJ11 (RS232)/Micro USB (RS232) along with optical port for reading  data  through  CMRI  and  AMR  modem.  Communication  ports  shall  not  be affected by any type of  injection/unauthenticated signals. The baud rate should not be less than 9600 bps and higher baud rate shall be preferred for down loading the data. The  complete data  shall be downloaded  within 5 minutes from meter to  CMRI &  from CMRI to BCS.

The bidder shall supply software required for local (CMRI) & remote (AMR) connectivity including required training to use the software free of cost. Both the communication ports work  simultaneously. The  bidder  shall  provide  meters  as  per  DLMS  compliance  i.e. meters with open protocol as per IS: 15959.

9

12.0	SOFTWARE:

Software for reading, down loading data of the meter and TOD programming in the meter, normally  resident  in  the  Common  Meter  Reading  Instrument  (CMRI),  software  suitable for MS-DOS 5.0 or higher version.

Windows  based  Base  Computer  Software  (BCS)  for  retrieving  data  from  CMRI  and downloading instructions from base computer software to CMRI. This  BCS should have, amongst	other	requirements	and	features	and	facilities	described	later	in	this specification, the facility to convert meter reading data into XML/ ASCII file format so that it  may  be  possible  for  the  user  to  integrate  the  same  with  the  user's  billing  data  and process the selected data in desired manner.

Necessary software for loading application program via CMRI serial port.

The following software shall be made available and installed on CMRI & BCS by the firm whose  meters  are  to  interface  with  CMRI  without  any  extra  charges.  Any  future  up gradation in both the software shall

be provided free of cost.

(a) Software to be resident in CMRI for the purpose of reading and programming the specific make(s) of static meters.

(b) Base computer stations (BCS) software for accepting data for CMRI, processing generating reports and down loading instruction from the BCS to CMRI. The firm shall   also   provide   ASCII   conversion   utility   along   with   BCS   software   for processing of the billing data.

(c) The firm shall install the above software without any extra cost on call from one of  the  Test  Division  located  in  each  of  the  Zones.  The  purchaser  will  arrange these  software  installations  in  rest  of  the  existing  and future  Test  Divisions for which  necessary  softcopies  with  appropriate  licences  shall  be  provided  by  the firm.

10

(d) It  should  not  be  possible  to  re-program  the  meter  at  site  (write  facility  through optical  port)  without  authenticated  password.  The  meter  programming  through optical  port  for  time  of  day  (TOD)  and  real  time  clock  (RTC).  Provision  for programming of TOD and RTC shall necessarily be provided.

(e) For efficient and speedy recovery of data read through CMRI, view & analysis, a Base  Computer Software  (BCS) shall have  to  be  supplied having  the following features:

The  BCS  software  shall  be  windows  based  user  friendly.  The  data  transfer  shall  be highly reliable and fraud proof. Base Computer software shall give all details adequate for  analysis  and  abnormal  event  data  &  load  surveys  parameters.  The  software  shall have   the  facility  to  convert  all   the  consolidated   information   /  data  of   selectable parameters into ASCII format. EDP department of purchaser can generate its own DBF

(data base files) to downloaded all the required information into it.

(i)	Platform:

The  BCS  shall  be  executable  on  WINDOW  XP  or  higher  updated  operating platform or higher operating system. The BCS shall be suitable to run on IBM PC or compatible hardware platform.

(ii)	Meter Data Display:

The  software  shall show electrical condition  existing  at  the  time  of  reading  the meter in  tabular forms as well as graphical format  (Phase  diagram with  phase angle).

All  the  information  about  energy,  maximum  demand  and  their  respective  TOD register reading, billing register readings shall be shown in a manner which user can easily understand.

All  the  load  survey  data  shall  be  available  in  numerical  as  well  as  graphical format. It shall be possible to view this data daily, weekly, and monthly format.

11

The  load  survey  graph  shall  show  values  where  the  cursor  is  placed  for  the selected or for all parameter.

All the information about abnormality events shall be accompanied with date and time  stamping  of  respective  electrical  conditions.  This  information  shall  be displayed in the sequence in which it happened in cumulative format as well as summary format.

BCS  should  display the  Date  and  Time  of  meter reading  in  the  computer.  The software  shall  be  capable  of  preparing  CMRI  to  read  the  meter  information  or time setting of the meter.

(iii)	Support Display:

There  shall  be  "user  friendly"  approach  for  viewing  meter  data  for  the  reading collected  now  or  for  the  reading  collected  in  the  past.  All  information  about  a particular  consumer  shall  be  sorted  out  and  available  at  one  place  so  that locating any consumer's past data is easy. It shall be possible to retrieve/locate data on the basis of either one of the following particulars:

a)	Site‘s ID/Numbers. b)	Meter Sr. No.

c)	Date of meter reading. d)	Location.

BCS of the bidder should support the supplied meters of it own make.

(iv)	The Data Transfer:

It shall be possible to transfer data to and fro from CMRI through serial interface.

(v)	Configurability:

It shall be possible to have selective print out of all available data of the meter. Print out shall not include anything and everything available with the BCS. The software shall support "print wizard" whereby user can decide what to print out.

12

The use of the software need not revert back to the supplier of the software for modifying the software just to print what he desires.

BCS  shall  have  facility  to  export  data  to  ASCII  or  spreadsheet  format  for integrating with the purchaser's billing system. Here again an "Export wizard" or similar utility shall be available whereby user can select file format, what data to export, the field width selection etc.

(vi)	Security:

The  BCS  shall  have  multilevel  password  for  data  protection  and  security.  The first level shall allow the user to enter the system. The different software features shall be protecting by different passwords. The configurable of passwords shall be  user  definable.  The  software  installed  on  one  PC  shall  not  be  capable  on another PC.

(vii)	Help:

The exhaustive online help shall be available with the software so that user can use all the features of the software by just reading the help contents.

Necessary software for loading application program via CMRI through serial port.

INTERFACE WITH MS DOS BASED CMRI:

For  Physical  interface  between  meter  and  Common  Meter  Reading  Instruments  shall consist of meters optical sensor terminating into a 9 Pin D type male connector with a cable of 500mm + 10mm length with a provision of reading the data without opening the meter box.

ILLUSTRATION NO.1

500mm long Cable	1500mm long Cable

Optical Port for connecting to Meter  9 pin Male	9 pin  female	Connection to CMRI The configuration of 9 Pin D type male connector shall be as given below:

PIN SIGNAL NAME

O5

O9	O4

O8	O3

O7	O2

O8	O1

01	NC

02	TRANSMIT DATA (TXD)

03	RECEIVE DATA (RXD)

04	NC

13

ILLUSTRATION NO.2

05	SIGNAL GROUND (SG)

06	NC

07	NC

08	NC

09	POWER SUPPLY

1500mm long Cable

Connection to CMRI	9 Pin Female connector to

Base Computer Station (BCS)

13.0	GENERAL REQUIRMEENTS:

13.1	Meter  shall  be  designed  and  constructed  in  such  a  way  as  to  avoid  introducing  any danger in use and under normal conditions so as to ensure specially the following:—

1.	Personnel safety against electric shock

2.	Personnel safety against effects of excessive temperature.

3.	Protection against penetration of solid objects, dust and water.

4.	Protection against spread of fire.

5.	Detection against fraud or pilferage.

There should not be any screws in the meter body through which meter can be opened and tampered without breaking the seal.

13.2	All the material used in the manufacture of meters shall be of highest quality. The entire design  and  construction  shall  be  capable  of  withstanding  stresses  likely  to  occur  in actual service and rough handling during transportation.

13.3	All  insulating  material used  is  the  construction  of  meter  shall  be  non-hygroscopic non ageing and of tested quality and will conform to tests as specified in relevant Standards. The  meter  shall  be  designed  on  application  specific  integrated  circuit  and  shall  be manufactured using SMT (Surface Mount Technology) components.

14

13.4	The  terminal  block,  the  terminal  cover  and  the  meter  case  shall  ensure  reasonable safety against the spread of fire. They should not be ignited by thermic overload of live parts in contact with them.

13.5	The   meter  shall   have   seamless  ultrasonically   welded   insulated  body,  along  with unidirectional  screws  and  wall  mounted  projected  type  to  be  fitted  with  the  help  of screws.

13.6		The  meter  shall  conform  to  the  degree  of  protection  IP51  of  IS:12063/IEC:529  for protection against ingress of dust, moisture and vermin.

13.7	All  parts  which  are  subject  to  corrosion  under  normal  working  conditions  shall  be protected effectively. Any protective coating shall neither be liable to change by ordinary handling nor damaged due to exposure to air under normal working conditions.

13.8	The	meters	shall	be	designed	such	that	their	working	remain	unaffected	by electromagnetic  interference,  electrostatic  discharges  and  high  voltage  transients  as specified in CBIP Report No. 325.

14.0	CONSTRUCTIONAL REQUIREMENTS:

14.1	METER CASE:

The meter shall have completely ultrasonically seamless type welded (in such a manner that  it  can  not  be  opened  without  breakage  or  crack)  insulated  body  and  be  of  wall mounted panel mounted projected type fitted with the help of screws and shall have a handle to facilitate carrying around. The meter shall have a case made of unbreakable high  grade  fire  resistant,  reinforced	polycarbonate  or  equivalent  high	grade engineering  plastic  which  can  be  sealed  in  such  a  way  that  the  internal  parts  of  the meter are accessible only after breaking the meter cover seals. The meter cover shall be fixed permanently and shall not be removable without the use of a tool. The meter shall have a transparent cover and opaque base with seamless ultrasonic welding. The meter cover shall have at least two sealing screws each screw having the sealing holes. These screws shall be made of brass and capable of being tightened from front.

15

The meter case shall have at least three mounting holes. Two holes for mounting screws on the terminal block sealed beneath the terminal cover and one for hanging screw on the top.

14.2	WINDOW:

The  meter  cover  shall  be  of  high  grade,  fire  resistant,  reinforced  polycarbonate  or equivalent high grade engineering plastic with one window made of UV stabilized, silicon coated  polycarbonate  or  equivalent  high  grade  engineering  plastic  for  reading  the register  and  observation  of  operation  indicator.  The  window  shall  be  of  transparent material  ultrasonically  welded  with  the  meter  cover  such  that  it  can  not  be  removed undamaged without breaking the meter cover.

14.3	TERMINALS AND TERMINALS BLOCK:

The base of the meter shall have a terminal block at the bottom made out of high grade engineering  plastic  so  as  to  facilitate  bottom  connection  and  houses  solid  zinc  plated brass terminals having capability to carry maximum value of current.

The  material  of  the  terminal  block  shall  be  capable  of  passing  the  tests  given  in  IS

14697: 1999/ CBIP -325.

The terminal holes in the insulating material shall be of sufficient size to accommodate the insulation of the conductors. The diameter of the terminal hole for current terminals shall not be less than 5.0 mm & shall be of adequate length in order to have proper grip of conductors / crimping pins with the help of two screws.

The terminal block shall satisfy all the conditions such as clearance & creepage distance between terminals & surrounding part of the meter as specified in relevant clause of IS

14697: 1999/ CBIP-88.

The manner of fixing the conductors to the terminals shall ensure adequate and durable contact  such  that  there  shall  have  no  risk  of  loosening  or  undue  heating.  Screw connections  transmitting  contact  force  and  screw  fixing  which  may  be  loosened  and tightened several times during the life of the meter shall be such that the risk of corrosion resulting from contact with any other metal part is minimised. Electrical connections shall

16

be  so  designed  that  contact  pressure  shall  not  be  transmitted  through  insulating material.

14.4	TERMINAL BLOCK COVER

14.5

The  terminals  block  cover  for  the  energy  meters  shall  be  extended  transparent  type, which  can  be  sealed  independently  of  the  meter cover.  The  ETBC shall have  a  clear space  of  min  40+5mm,  thus  allowing  sufficient  clearance  space  for  inserting  cables. ETBC  shall  have  a  top  side  hinge  arrangement  for  easy  access  of  terminal  for  wire termination.  The  terminals, their fixing  screws and  the  insulated  compartment  housing them shall be enclosed by extended terminal cover in such a way that no part of meter or accessories at terminal block shall be accessible from the front of  the meter. There shall be provision of fixing of seals so that screws cannot be loosened without breaking the seals.

The  terminals  shall  not  be  accessible  without  removing  the  seal(s)  of  terminal  cover when energy meter is mounted on the meter board.

The  meter  shall  have  nickel  plated  brass  terminals  suitable  for  termination  of  internal wiring (HT TVM), which may be grouped in terminal block, having adequate insulating properties and mechanical strength. The terminal block shall be made from best quality non-hygroscopic,  fire  retardant,  (capable  of  passing  the  flammability  tests given  in  IS:

11731),  reinforced  polycarbonate  (not  bakelite)  or  equivalent  high  grade  engineering plastic which should form an extension of the meter case. It shall have terminal holes of adequate  length  and  of  minimum  internal  diameter  5.0  mm  to  accommodate  the insulation of the conductors and shall have proper grip of conductor with the help of two screws in each current terminals to ensure adequate and durable contact such that there is no risk of loosening or undue heating. Screws connections transmitting contact force and screw fixing which may be loosened and tightened several times during the life of the  meter,  shall  screw  into  a  metal  nut.  Each  clamping  screw  shall  engage  atleast  3 threads in the terminals. The screws shall not have pointed edge at the end of thread. The  clearance and  creepage  distance of  terminal block and tips between  the  terminal and the surrounding parts of metal enclosure shall be as per ISS.

17

All parts of each terminal shall be such that the risk of  corrosion resulting from contact with any other metal part is minimized.

Electrical   connections   shall   be   so   designed   that   contact   pressure   is   not transmitted through insulating material.

14.6	OUT PUT DEVICE:

The  meter shall be  have  a test output accessible form the front  and  capable  of  being monitored with suitable testing equipment. The operation indicator, must be visible from front. However, it shall be possible to check the accuracy of energy measurement of the meter  in  the  field  by  means  of  LED  output  on  meter.  Meter  should  have  One  /  Two calibration  LEDs  for  accuracy  measurement  for  different  energies.  Out  of  these,  one should be kept fixed on  kWh and other one shall be  configurable for rest two  (kVArh, kVAh). Resolution of the test output shall be sufficient to enable the starting current test in less than 10 minutes

14.7	TERMINAL COVER:

The meter terminal Block shall be provided with an extended terminal cover which may be transparent with independent sealing arrangement in such a way that it shall cover the terminals, the conductor fixing screws, the external conductors and their insulation .

When the meter is mounted, no access to the terminals shall be possible without breaking the seal of the meter terminal cover and arrangement shall be made to fix the terminal cover permanently.

The terminal cover shall have two sealing screws independent of each other. The fixing screws used on the terminal, cover for fixing and sealing shall be kept captive in the terminal cover.

14.7	TERMINAL ARRANGEMENT:

The terminals shall be marked properly on terminal block for giving external connections. A diagram of  connections should be provided inside the cover the terminal block. The terminal cover shall be extended such that when it is placed in position it is not possible to approach the connections or connecting wires.

18

14.8	CONNECTION DIAGRAM:

Every  meter  shall  be  indelibly  marked  with  connection  diagram  showing  the  phase sequence for which it is intended and shall be attached to the inner-side of the extended terminal block cover. In case of any special precautions need to be taken at the time of testing the meter, the same may be indicated alongwith the circuit diagram.

14.9	SEALING OF METER:

Meter cover should be physically joined by seamless ultrasonic welding in such a way that meter cover cannot be opened without breaking and shall be physically evident as well as it should be logged as tamper event in case cover is opened. Reliable sealing arrangement should be provided to make the meter tamper evidence and avoid fiddling or   tampering   by   unauthorized   persons.   For   this,   at   least   two   (2)   Nos.   sealing arrangement on meter body, one (1) No. sealing arrangement on meter terminal cover and one (1) No. sealing arrangement on communication port shall be provided. All the seals  should  be  provided  on  front  side  only.  We  have  noted  that  rear  side  sealing arrangement  shall  not  be  preferred.  The  suppliers  in  their  offer  should  explain  the sealing arrangement.

14.10   NAME PLATE MARKING:

Every  meter  shall  be  provided  with  a  Laser  printed  name-plate  which  shall be  clearly marked/embossed  as  per  clause-7  of  IS:14697/1999.  The  name  plate  shall  have following  markings  which  shall  be  indelible,  distinct  and  readable  from  outside  the meter:—

(a)	Purchaser’s	name,	Purchase	order	No.	and	date	with	inscriptions	&

"PROPERTY OF PVVNL".

(b)	Manufacturers name, Trade mark and place of manufacturer.

(c)	Design & type.

(d)	Nature of current and no. of phases and no. of wires for which meter is suitable for.

(e)	The  manufacturers  serial  no.,  year  of  manufacture  and  warrantee  period.  The serial no. is also to be marked on the meter base.

(f)	Reference voltage

(g)	Reference current

(h)	Meter constant (if any)

19

(i)	Class of accuracy

(j)	Reference temperature

(k)	Transformation ratios of instrument transformers (s) of which account is taken for meter constant.

15.0	TAMPER AND FRAUD PROTECTION:

15.1	The  meter should  have facility to detect the  occurrence  and  restoration  with  date  and time of atleast the following common ways of tamper and frauds. The meter shall also have  the facility to  indicate/log  at  BCS  end snap shot  of  parameters i.e. voltage  of  all Phases, Current of all phases, P.F. of all phases, KWH on occurrence and restoration of tamper.

a)	PHASE  SEQUENCE  REVERSAL:  The  meter  should  work  accurately  irrespective  of phase sequence of the supply.

b)	C.T. POLARITY REVERSAL:

The meter shall detect C.T. polarities reversal and record the same, with date and time of  first  occurrence  and  last  restoration  alongwith  total  no.  of  such  occurrences  for  all phases during the above period.

c)	MISSING POTENTIAL:

The meter shall be capable of recording occurrences of missing potential (1 phase or 2 phases)	and	its	restoration	which	can	happen	due	to	intentional/	accidental disconnection   of   potential   leads   with   date  and   time   alongwith   total  no.  of   such occurrences for all phases during the above period. This recording of tamper shall not be done when meter is without any load i.e. current in all phases is Zero.

d)  CURRENT UNBALANCE:

The  meter  shall  record  with  date  and  time  when  the  load  unbalanced  exceeds  the specified threshold limit.

e)	INFLUENCE OF HIGH MAGNETIC FIELD:

The performance of meter should not be affected under the influence of external DC/AC

magnetic field of high intensity as mentioned in CBIP Technical Report-325. Meter shall

20

start recording fast energy at Imax in case of placement of magnet on any part of meters body i.e. front or back or top or bottom etc as per the latest amendment of CBIP ‘325.

f)	Cover Open tamper: Logging of cover open tamper through tamper switch

placed inside the meter and shall communicate signal to display LCD as well recorded in  memory of  MRI.  The  meter shall be able  to detect  cover open occurrence event  if cover  is  opened  in  mains  on  or  off  condition.  Separate  legend  for  cover  open  event shall be made available on LCD. This legend shall remain in on state till meter reading so that it will come in to notice of meter reader.

g)   Neutral  Disturbance  –  The  meter  should  detect  neutral  disturbance  if  any  spurious signal is applied at the meter’s neutral.

h)	ABNORMAL VOLTAGE/FREQUENCY DEVICE TEST:

The  accuracy  of  the  meter  would  not  be  affected  with  the  application  of  abnormal voltage/  frequency  generating  device  having  spark  discharge  of  approximately  35KV. The  meter  will  be  tested  by  feeding  the  output  of  this  device  to  meter  in  any  of  the following manner for 10 minutes:

i)	On any of the phase or neutral terminals.

ii)	On any connecting wires of the meter.

iii)	Voltage discharge with 0-10 mm spark gap.

iv)	Spark on meter body.

v)	Spark on the optical and RS 232 port.

vi)	At any place in load circuit.

15.2	TAMPER INFORMATION/LOGIC:

The  tamper  logic  in  the  TVM's  shall  be  capable  of  discriminating  known  system abnormalities from source  side  and  load  sides and  shall not  log/record  tamper due  to source side abnormalities.

Minimum last 300 events (occurrence + restoration) of total tamper events with day and time shall available through CMRI and all these information shall be available in simple and early understandable format. It shall be possible to retrieve the tamper data through optical port to CMRI. The firm should furnish the details as to how these meter is able to

detect protect/record about tamper and fraud features with sketches and phaser diagram

when ever necessary.

21

NOTE:

i)	The  meter  design  should  take  care  of  all  the  possible  tamper  methods  and  the

"Purchaser" will not accept the external arrangements like external box cover etc.

ii)	All the tamper features shall be tested in routine inspection of meters in each offered lot and shall be part of Routine/Acceptance test.

iii)  The tamper event recording shall be roll over type for each individual compartment. The latest/  last  tamper  event  shall  be  logged  and  earliest  event  will  disappear  in  each compartment. Tamper occurrence and restoration shall be counted as separate event.

15.3	TAMPER PERSISTANCE TIME:

The persistence time of logging of an occurrence of tamper shall be three minutes. The persistence time for logging of restoration of tamper shall be two minutes. Provision shall

be  made  for  logging  voltage  of  all  phases,  current  of  all  phases  ,  power  factor  of  all

phases, KWH and KVAH on  occurrence and restoration of tamper at BCS end..

16.0	DRAWING AND MANUAL

16.1	The  firm  is  required  to  submit  one  copy  of  drawing  and  manual  with  the  tender documents and in each packing case of energy meters for use of field offices.

16.2	Maintenance  and  repair  manuals  including  instructions  for  testing  adjustments  and calibration shall be submitted with the contractual documents.

17.0	INSPECTION AND TESTING:

17.1	Each lot of meters offered for supply shall be inspected for routine/ acceptance and  anti tamper feature  test  at  manufacturers'  works to  verify that  these  are  being  supplied  in accordance  with  relevant  standards/  technical  specification  and  guaranteed  technical particulars.

17.2	At  the  times  of  inspection  and  testing  the  firm  shall  however  submit  all  routine  test results of all meters offered, to the inspection officer.

17.4	All instruments used in inspection and testing should be properly calibrated and sealed once  a  year.  Calibration  Certificate  when  demanded  by the  inspecting  officer shall be provided   /   produced  for   verification   purposes.   In   case   of   any   dispute   regarding calibration, instruments shall be sealed and signed by the representative of the firm and purchaser  and  will  be  sent  to  test  house  Government  lab/  Government  Institution  of repute, for calibration at the cost of firm.

22

17.5	Purchaser reserves the right to get the meters inspected/ tested before dispatch by any

Independent Inspecting Agency, at the cost of purchaser.

18	TYPE TEST:

18.1	SCHEDULE OF TYPE TEST SHALL BE AS FOLLOWS:

18.1.1  TEST FOR MECHANICAL REQUIREMENTS:

(a)	Vibration Test

(b)	Shock Test

(c)	Spring hammer test

(d)	Protection against penetration of dust and water

(e)	Test of resistance of heat and fire

18.1.2  TEST FOR ELECTRICAL REQUIREMENT

(a)	Test of power consumption

(b)	Test of influence of supply voltage

(c)	Test of influence of short time over currents

(d)	Test of influence of self heating

(e)	Test of influence of heating

(f)	Test of influence of immunity of earth fault

18.1.3  INFLUENCE OF INSULATION PROPERTIES:

(a)	Impulse voltage test

(b)	AC High voltage test

(c)	Insulation test

18.1.4  TEST OF ELECTROMAGNETIC COMPATIBILITY:

(a)	Radio interference measurement

(b)	Fast transient burst test

(c)	Test of immunity to electrostatic discharge

(d)	Test of immunity to electromagnetic H.F. field

18.1.5  TEST OF ACCURACY REQUIREMNT:

(a)	Test of limits of error

(b)	Interpretation of test results

(c)	Test of meter constant

(d)	Test of starting conditions

(e)	Test of no load conditions

(f)	Test of ambient temperature influence

(g)	Test of repeatability of error

(h)	Test of influence quantities

18.1.6  TEST FOR CLIMATIC INFLUENCE

23

(a)	Dry heat test

(b)	Cold test

(c)	Damp cyclic test

18.1.7  INFLUENCE  OF  HIGH  MAGNATIC FIELD  AS PER CBIP  TECHNICAL REPORT  NO.

88 (REVISED JUNE 2000 OR LATEST REVISION) Read with 3rd  amendment/Errata

Feb. 2002

Meter  shall  be  provided  with  appropriate  magnetic  shielding  so  that  any  external magnetic field (A.C. electromagnet or D.C. magnet) as per the values specified in CBIP report no. 325, applied on meter would not affect the proper functioning of meter.  Also  when  magnetic field  such  as 0.5  Tesla  is  applied  on  the  meter  (which  is above the immunity level as defined in CBIP report), it shall record at I max. at UPF. Influence  of  Spurious  signal  :  The  meter  should  record  accurately  in  case  of  DC  or spurious signal through neutral and meter should log such condition with date and time if influenced.

Note: Any other type test if included in IS/IEC/CBIP standard (latest revision) or test as per revised limits have to be done on PROTO-TYPE sample meter.

19.0	The  firm  shall  supply  the  meter  as  per  specification/drawing  as  type  tested.	If  any change  in the design/parameters is being  made, then the  meter shall have to be type tested again at the cost of the firm.

20.0	ROUTINE TEST:

All  the  meters  offered  for  supply  shall  be  tested  by  the  manufacturers  at  their works  so  as  to  conform  that  these  are  being  manufactured  in  accordance  with  the technical  specification/ISS.	A  copy  of  these  routine  test  results  shall  be  enclosed alongwith the packing list at the time of offering the material for inspection.

21.0	ACCEPTANCE TESTS:

Shall consist of the following :

(a)	A.C. Voltage test

(b)	Insulation resistance test

(c)	Test on limits of errors

(d)	Test on meter constant

(e)	Test on starting condition

(f)	Test of no-load condition

(g)	Repeatability of error test

(h)	Test of power consumption

(i)	Vibration test

(j)	Shock test

24

(k)	Tamper proof test

22.0	OTHER GENERAL REQUIREMENT:

(a)	The  meter  shall  be  designed  in  a  way  to  ensure  continuity  of  supply  and reliability, providing facilities for inspection, testing and calibration, maintenance and repair.   They shall operate without undue vibration and the least amount of noise.

(b)	They  must  so  designed  to  be  unaffected  by  normal  sea,  air  or  land  transport requiring no recalibration before, installation and routine or type tests.

(c)	The frame supporting metering elements shall be unique, single piece sufficiently rigid.

23.0	(a)	Material shall be packed generally in accordance with clause 9.1 (Annexure-E) of

ISS: 13010:1990.

(b)	Accompanying   devices   and   accessories   shall   be   placed   inside   a   shock absorbing, protective carton box or expanded polystyrene moulding.  One carton box or expanded polystyrene moulding may be used to accommodate not more that five Nos.  Energy Meters.

(c)	The  meters  and  devices  in  boxes  or  mouldings  shall  be  carefully  packed  for overseas shipment in sturdy wooden cases capable to be stored outdoor without further protection against weather conditions (Rain or humidity).

(d)	Meters  in  the  original  packing  shall  be  unaffected  by  normal  sea,  air  or  land transport and should be ready to be installed and operate reliably and accurately immediately after unpacking.

24.0	SPARE PARTS:

(a)	Availability of spare parts shall be guaranteed by the firm for a period of 10 years after the delivery of each items.

(b)	The  firm  or  their  collaborators  or  their  authorised  agents  should  have  service facilities  alongwith  adequate  spare  parts  in  India  to  provide  prompt  service initially for a period of 10 years.

25.0	AFTER SALES SERVICE:

After  Sales  Services,  as  and  when  required  shall  be  provided  by  the  firm  to  the purchaser  directly  through  their  own  qualified  Engineer  and   it   will   also  be  their responsibility   to   educate   PVVNL   staff   by   demonstration   and   detailed   technical instruction as mutually agreed upon at different sites (Zonal Headquarters) in the State of U.P. for 42 months from the date of last dispatch.

26.0	TECHNICAL SPECIFICATION AND GUARATNEEED TECHNICAL PARTICULARS:

25

The material shall be manufactured and tested in accordance with specific requirement of  this  specifications  of  Static  Trivector  Meters  and  Guaranteed  Technical  Particulars

(GTP).

27.0	METHOD/PROGRAMME TO BE ADOPTED FOR LOADING OF METER SOFTWARE

PROGRAMME IN MS DOS BASED METER READING INSTRUMENTS:

It shall be the responsibility of the supplier to load their software programme in MS DOS Based  CMRI  of  any  other  make,  on  the  Computer  installed/to  be  installed  in  various office of  UPPCL  as per request  received directly from field units or Purchaser without any extra charges.

The  coordination for this purpose  between  supplier of  MS  DOS  Based  CMRI's and Static Trivector Meter respectively, shall be made by purchaser.

28.0	PERIOD OF GUARANTY AND PERFORMANCE:

(a)	The firm shall undertake a guarantee for 60 months from the date of installation and 66 months from the date of  supply, replace within one month of  receipt of report  of  the  meters,  which  are  found  defective/  inoperative  at  the  time  of installation.  (This clause should be read with clause should be read with clause No. 1.2.5 of instructions to tenderers/ clause 30 of Form B.

(b)	In  case  of  any  discrepancy  between  the  specification  and  relevant  standards, previsions contained in this specification shall prevail.

**********************

26

GUARANTEE TECHNICAL P ARTICULARS 11KV HT TVM THREE PAHSE FOUR WIRE, -/5A WITH DLMS (CAT.- C)&  33KV HT TVM THREE PAHSE FOUR WIRE, -/1A WITH DLMS (CAT.- C)

Sl.No.	Particulars

1	2	3

1	Makers Name

2	Make

3	Type of Meter/Design

4	State the year since the design is in vogue

5	Standard to which meter conforms

6	Class of Accuracy

7	Rated current (Amps)

8	Rated maximum current as percentage of basic current

9	Rated voltage, volt

10	Rated Frequency, Hz

11	Specified operating voltage range

12	Limit voltage range of operation

13	Reference temperature

14	TEMPERATURE RANGE OF OPERATION

(a) Specified operation range

(b) Limit range of operation

© Limit range for storage & transport

15	RELATIVE HUMIDITY

(a) Annual mean

(b) For 30 days these days being spread in a natural manner over the year

© Occasionally on other days

16	POWER CONSUMPTION

(a) Power consumption in voltage circuit at rated current

27

(i) Active in watts

(ii) Apparent in VA

(b) Power consumption in current circuit (in VA) at rated current

17	Current that meter is capable of carrying continuously without injury to the meter (Amps)

18	Short Time over current capability of the Meter

19	Percentage minimum current which shall start the meter and continue to run thereafter at rated voltage and unity power faction (% of basic current)

20	Type of material along with its thickness or dimensions (in mm) and details of the important components parts of the meter

(b) Terminal covers

© Terminals

21	Size of terminal holes

22	No. of earthing terminals provided on the body of the meter, if any

23	Whether toughened glass window is provided

24	Whether carrying handle is provided

25	Meter constant (if any)

26	Tamper & Fraud Protection details

Stated whether as per specification or not

a) Phase sequence reversal

b) CT Polarity reversal

c) Missing Potential

d) Current Unbalance

28

e) Whether tamper information/logic have been provided as per specification

f) Whether meter is tamper proof against influence of high magnetic field as per CBIP 325

27	a) Display type (LCD)

b) No. of digits in display

c) Display Cycle

d) Scroll lock facility provided or not

28	a) Are the parameters as specified in clause of specification available on display/ measuring

b) Specify other parameters/quantities which may be available on display without any extra cost

29	a) Is the meter capable of measuring and storing the data as per clause of the specification

b) Other information in memory available through

CMRI without any extra cost

30	a) Specify the tamper data available on the display of the meter

b) Specify the tamper data available through

CMRI

c)Specify time duration of meter data downloading

through CMRI from meter.

d) Whether Optical port is compatible with SANDS

& Analogic make CMRI or not

31	Self Diagnose

a) On Display, if any

b) On Memory

32	Sealing Arrangement (Specify)

Whether sealing at the following has been provided

a) Body of the Meter

b) Terminal cover of the meter

c) Optical port

29

d) Power pack unit port

33	Overall dimensions of the Meter (with tolerance)

a) Height (mm)

b) Width (mm)

c) Depth (mm)

34	Total weight of the meter (kg) with tolerance

35	State Whether

a) Load survey capability of 35 days have been provided as per of Technical Specification

b) Time of day zones have been provided as per clause of technical specification

30