## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-I, Noida
Name of Work: DETAILS OF WORK AND QUANTITY AGAINST SHORT TERM E-TENDER NO. 02/EUDC-I/2023-24/NOIDA (WORKS) FOR CARRYING OUT THE BIFERCATION OF 11 FEEDER NO. 4 EMANATING FROM 33/11 KV S/S SECTOR-67, NOIDA IN AREA OF EUDSD-IV, NOIDA UNDER EUDD-I, NOIDA IN THE JURIDICTION OF EUDC-I, NOIDA.
Contact No: 0120-2970431
GST Will be paid Extra as per norms.
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) Note:- 1. Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC. 2. Payment will be done after complete execution of work/ entire project & submission of executed estimate and after getting satisfactory report in all respect from concern SDO/JE.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | FOLLOWING WORK BIFERCATION OF 11 FEEDER NO. 4 EMANATING FROM 33/11 KV S/S SECTOR-67, NOIDA IN AREA OF EUDSD-IV, NOIDA :- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | Cartage of ST poles 11 mtr long from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Cartage of other line material such as 11 KV HT XLPE Cable 3x185 Sq.mm. (240 Mtrs.), MS channel (Dropper) 100x50x2000mm (01 No.), MS Top Channel 100x50x2240mm (01 No.), 11KV Com. Poly Pin Insulator (06 Nos.), 11 KV Fuse Set (1 Nos.) etc. from ESC Noida/Sahibabad/Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to site of work including loading and unloading at both ends. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.03 | Fabrication & fixing of MS channel / Angle complete in all respects. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | The Excavation of foundation pit in CC road/ mix soil/ normal soil/ soft & hard rack by using heavy duty compressor and its back filling and leveling etc. The size of the pit will be 600x600x1800 mm for each pole and having a depth of 1/6 of the full length of the support. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | Erection of Double Pole on 11 Mtr. long ST Pole for 11 KV line including fixing of all accessories of 11 KV line as per RESPO schedule Complete in all respects. |  | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.06 | Grouting of each pole (In ratio of 1:4:8 in Cement, sand and Brick Ballast) in size 450mmx450mmx1800 mm as per RESPO schedule Complete in all respects. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.07 | Construction of Plinth in size 450x450x300 mm of each (0.285 Cum) pole above the ground level (In ratio of 1:3:6 in Cement, sand and Brick Ballast) as per RESPO schedule Complete in all respects. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.08 | Laying of 11 KV XLPE Cable 3x185 Sq.mm. through open trench, digging of proper trench, laying of above Cable, putting sand around the cable. Fixing of bricks in both sides & top and refilling of trench and its proper ramming including providing necessary loop on both sides, connecting of cable as per site requirement and RESPO norms. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 240 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.09 | Providing of Holding clamp with bolt & Nuts. |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.1 | Fixing of above Holding clamp with bolt & Nuts. |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.11 | Providing of 11 KV Fuse set complete of best quality as per requirement for completion of work due to not available in store. |  | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.12 | Installation of above 11 KV Fuse Set with required items complete in all respect. |  | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.13 | Providing of 11 KV Outdoor / Indoor jointing kit of Raychem/ 3M/ Denson make suitable for 11 KV 3x185 sq.mm. XLPE cable |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.14 | Fixing of above 11 KV Outdoor / Indoor jointing kit of Raychem/ 3M/ Denson make suitable for 11 KV 3x185 sq.mm. XLPE cable |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.15 | CARRIAGE OF NEW 11 KV INDOOR TYPE V.C.B. O/G 300/150/5A FROM GHAZIABAD/ SHAHIBABAD/NOIDA/JE STORE TO SITE OF WORK WITH SAFE LOADING AND UNLOADING AT BOTH ENDS. |  | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.16 | LABOUR CHARGES FOR ERRECTION OF ABOVE NEW 11 KV INDOOR TYPE V.C.B. O/G 300/150/5A WITH CONNECTING 11 KV OUTGOING CABLES, FIXING OF EARTHING AND WIRING AS REQUIRED IN VCB, ALL TESTING OF NEW VCB ETC WITH PROPER SAFETY TO COMPLETE THE WORK ETC IN ALL RESPECT. |  | 1 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.17 | PROVIDING AND INSTALLATION OF CHEMICAL EARTHING FOR NEW VCB BRAKER (WITH ALL MATERIAL AND LABOUR) AFTER INSTALLATION RESISTANCE SHOULD BE LESS THAN ONE OHM. AS PER FOLLOWING :- Note :- The all material and labour shall be provided by the contractor with 12 month guarantee for resistance value less than one OHM and should be checked 06 months after proper installation. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.18 | Providing of earth elctrode for chemical earthing Pipe in pipe type proper hot deep galvanization dia 80 mm length 3 mtr - 50mm x 6mm terminal connection hole dia 8mm The cavity between the pipe & pipe is filled with conductive mixture - for hermetically filling inside the cavity i.e. between secondary conductor & primary conductor, crystalline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc the electrode should be sealed from both the ends. The outer pipe of the elctrode should be galavanized the characteristics of this compound is highly cnductive, non magnetic & non corrosive in G.I. Including providing of backfill compound each elctrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested for new 11 KV VCB Braker. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.19 | Providing and fixing of GI strip of size 50 mm x 6 mm suitable for new 11 KV VCB Braker. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.2 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information