## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle, Hapur.
Name of Work: FOR SHIFTING OF ELECTRICITY LINE AND OTHER ASSOCIATED WORKS, DUE TO SUDRADHIKARAN AND WIDENING OF MEERUT-BULANDSHAR MARG, IN DEPOSIT SCHEME, IN THE JURISDICTION OF EDD-I HAPUR, UNDER EDC., HAPUR.
Tender No: 138(W)/EDCH/2023-24
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | FOR SHIFTING OF ELECTRICITY LINE AND OTHER ASSOCIATED WORKS, DUE TO SUDRADHIKARAN AND WIDENING OF MEERUT-BULANDSHAHAR MARG, IN DEPOSIT SCHEME, IN THE JURISDICTION OF EDD-I HAPUR, UNDER EDC., HAPUR. | BI01010001010000000000000515BI0100001112 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | Carriage of line material (like channel, agnle, clamp, earth rod, stay rod, ACSR Conductor etc.) from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001113 | 55.77 | Qtl. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Carriage of ST Pole 11 mtrs. Long from Electricity store center, Hapur/J.E. Store to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 169 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.03 | Carriage of 11KV XLPE Cable 3x185Sqmm. from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 1740 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.04 | Carriage of LT ABC(3x120+1x95+1x16) Sqmm. from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 3250 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | Carriage of LT XLPE cable 1x400Sqmm. from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 400 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.06 | Carriage of Cable jointing Kit from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 56 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.07 | Carriage of Distribution Box single Phase from Electricity Store Center, Hapur to site of work with loading and unloading at both ends on Kachha Packka road. | BI01010001010000000000000515BI0100001115 | 60 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.08 | Erection & Fixing of ST Pole 11 mtr. long in LT. line after digging of suitable pits including fixing of requisite all accessories as per RESPO Drawing/Norms by providing L.T. Pin Clamps, M.S. Flat of size 50x6 & Schacle Insulator of size 75x90mm, with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 25 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.09 | Erection & Fixing of STP Pole 11 mtr. long in 11 KV line after digging of suitable pits including fixing of requisite all accessories as per RESPO Drawing/Norms by providing F-Bracket and holding Clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts. | BI01010001010000000000000515BI0100001115 | 98 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.1 | Erection of double pole structure with all accessories on ST Pole 11 mtr. long, fabrication and fixing of M.S. Top & Dropper Channel, M.S. T/F Angle, E-Bracket, 11 KV Pin insulator with Pin, Disc Insulator with Disc fitting etc., as per RESPO Drawing/Norms by providing all clamps made of M.S. Flat of size 50x6 mm with proper size nuts and bolts, and jumpering etc work. | BI01010001010000000000000515BI0100001115 | 23 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.11 | Laying , Stringing and final sagging of ACSR Dog Conductor after binding from Insulator, as per RESPO/Drawing Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 9420 | mtrs. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.12 | Laying of LT ABC (3x120+1x95+1x16)sqmm and completion work properly, as per RESPO/Norms., and reconnetion of service line properly as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 3250 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.13 | Laying of LT XLPE Cable 1x400sqmm and completion work properly, as per RESPO/Norms., including by provinding fitting all accessories. as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 400 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.14 | Laying of 160mm O/D PN-4PE-80 PN-4 grade UV stabilized HDPE pipe as per IS of 6meter, for laying of underground Cable as per RESPO/Norms, including cost of above HDPE pipe. | BI01010001010000000000000515BI0100001115 | 900 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.15 | Laying of 11KV XLPE Cable undergound (870x2=1740 Double Circuit) into HDPE Pipe, spare cable shall be left in the loop shape at both ends as per RESPO/Norms and as per direction of site incharge | BI01010001010000000000000515BI0100001115 | 1740 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.16 | Digging of earth and refling with road restoration Kaccha charge for as per RESPO/Drawing Norms. (The Firm will be fully responsible for this work and taking necessary permission) | BI01010001010000000000000515BI0100001115 | 150 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.17 | Digging of earth and refling with road restoration Pakka charge for as per RESPO/Drawing Norms. (The Firm will be fully responsible for this work and taking necessary permission) | BI01010001010000000000000515BI0100001115 | 150 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.18 | Making and filling of 11KV Cable Jointing Kit, 3x185sqmm. Outdoor type, after duly plumbing and taping of suitable XLPE Cable, providing, fixing and crimping of proper size good quality lugs, including cost of lugs and tape etc., as per RESPO Norms and as per direction of site incharge | BI01010001010000000000000515BI0100001115 | 56 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.19 | Erection & Fixing of Distribution Box on pole by provding 02 Nos. D/B Clamps & proper size nut & bolts, as per RESPO Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 60 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.2 | Providing & Fixing of G.I. pipe 6"dia Class-B over 11 KV 3X185 Sq.mm XLPE cable before mounting the cable at double pole. The work includes fitting of clamps, sealing of top and bottom of pipe and one end of pipe is to be burried under earth about 500mm earch including mounting and clamping the cable on double pole structure and making connection with overhead line at both ends. | BI01010001010000000000000515BI0100001115 | 360 | mtrs | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.21 | Grouting & fixing of stay rods (16x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:4:8 cement, sand, 40mm brick ballast as per drg. Including back filling, proper ramming etc and fixing tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing as per RESPO Drawing/Norms by providing all grouting material and stay clamp made of M.S. Flat of size 50x6mm with proper size bolts & nuts & loops. | BI01010001010000000000000515BI0100001115 | 45 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.22 | Earthing of supports with MS earth Rod of (20x2540)mm long including excavation of pit and driving M.S. Rod 3.0 M apart from support and 0.5m below the ground level and connection below the earth electrodes with the help of G.I. wire & earthing lugs as per RESPO Drawing/Norms by providing proper size nuts & bolts. | BI01010001010000000000000515BI0100001115 | 169 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.23 | Grouting of ST/PCC supports in CC 1:4:8 (Cement, sand & 40mm brick ballast) Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, up to ground level, 300mm plinth above the ground level with CC 1:3:6 (Cement, core sand and Stone grit) with mufting as per drawing, work includes back filling & proper ramming by providing all required grouting materials. | BI01010001010000000000000515BI0100001115 | 169 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.24 | Construction of T/F plinth suitable for 250KVA T/F (size of 2 x 2 x 1.5 mt.) as per drawing, cc work in foundation in ratio 1:4:8 (Cement, Sand & Brick ballast). Ist class brick work in side walls cc ratio of 1:4 (cement & fine sand). 12mm thick plaster in ratio 1:4 (cement & fine sand). The RCC work on top of plinth in ratio 1:2:4 after duly filling of brick ballast inside the plinth & ramming the same, including cost of all material & labour. | BI01010001010000000000000515BI0100001115 | 9 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.25 | Construction of T/F plinth suitable for 400KVA T/F (size of 3 x 2 x 1.5 mt.) as per drawing, cc work in foundation in ratio 1:4:8 (Cement, Sand & Brick ballast). Ist class brick work in side walls cc ratio of 1:4 (cement & fine sand). 12mm thick plaster in ratio 1:4 (cement & fine sand). The RCC work on top of plinth in ratio 1:2:4 after duly filling of brick ballast inside the plinth & ramming the same, including cost of all material & labour. | BI01010001010000000000000515BI0100001115 | 6 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.26 | Construction of safety fencing (MS) for Transformer 11/0.4 KV Sub Station, With supply of material required for MS fencing (50X50X3 MM) M.S. wire mesh construction utilizing vertical post duly grouted/fitted in ground/on floor. Horizontal angle/T-iron to be fitted on vertical posts. Pickets (if required) fitted to rail and gate to facilitate entry and exit. The vertical Posts/Horizontal post shall be made of M.S. angle 75x75x6mm. Such post shall be kept preferably at distance of 800-1000 MM. and shall be grounded with CC ratio 1:4:8. The length of vertical post shall be sufficient to take care of fencing as requirement at site, and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 15 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.27 | Providing and installation of maintenance free multifaceted proactive and corrosion free chemical earthing electrod size 80mm x 3000mm complete with 50KG backfill compound with all required accessories for Body earthing of Transformers, including cost of M.S. earth strip for connection the earth strip will be welded to the earthing and neutral support, as per RESPO/Norms and as per direction of site incharge. | BI01010001010000000000000515BI0100001115 | 30 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.28 | Erection & Fixing of 11KV. Fuse set on ST Pole 11mtr long, by providing all required materials, including cost of 11KV Fuse set. |  | 15 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.29 | Providing and fixing of Suspension Clamp with Eye Hook as per RESPO/Norms and as per direction of site incharge. |  | 115 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.3 | Providing and fixing of Dead End Clamp with Eye Hook, as per RESPO/Norms and as per direction of site incharge. |  | 45 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.31 | Providing & fixing of Copper L- Pieces 62x225x12mm as per RESPO/Norms and as per direction of site incharge. |  | 60 | No. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.32 | Installation/Erection of 4-Core L.T. MCB with Box, including providing of the same and Completion of properly work as per RESPO Norms and as per direction of site incharge. |  | 15 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.33 | Shifting of 400KVA T/F-06Nos., and 250KVA T/F-04Nos., including Removal/mounting and completion work properly as per RESPO Norms and as per direction of site incharge. |  | 10 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.34 | Shifting of 63KVA T/F-02 and 100KVA T/F-05Nos., including Removal/mounting and completion work properly as per RESPO Norms and as per direction of site incharge. |  | 7 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.35 | Dismantling & Removal of old existing STP/Rail pole after digging of pit and opening of all accessories. |  | 118 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.36 | Carriage of STP/Rail Pole form site of work to JE Store/ESC-Hapur, with loading and unloading at both ends on Kachha Packka road. |  | 118 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.37 | Dismantling of existing Line and old & used conductor and service connection cable, opening of all accessories. (Iron Scrap 1500Kg., Weasel-1076Kg., and LT cable scrap-1950kg, including carriage of above material form site of work to JE Store/ESC-Hapur, with loading and unloading at both ends on Kachha Packka road. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
1.38 | Jumpering and line energisation work properly as per RESPO/Norms. |  | 2 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE!
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information