## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-I, Noida
Name of Work: DETAILS OF WORK AND QUANTITY AGAINST SHORT TERM E-TENDER NO. 53/EUDC-I/2022-23/NOIDA (WORKS) FOR CARRYING OUT THE WORK REPLACEMENT OF DAMAGED & NON REPAIRABLE 33/11 KV VCB SITUATED AT 33/11 KV S/S SECTOR-62 GREEN BELT, NOIDA IN THE AREA OF EUDSD-II, NOIDA UNDER EUDD-VII, NOIDA IN THE JURIDICTION OF EUDC-I, NOIDA.
Contact No: 0120-2970431
GST Will be paid Extra as per norms.
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) Note:- 1. Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC. 2. Payment will be done after complete execution of work/ entire project & submission of executed estimate and after getting satisfactory report in all respect from concern SDO/JE.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | FOLLOWING WORK EPLACEMENT OF DAMAGE & NON REPAIRABLE 33/11 KV VCB SITUATED AT 33/11 KV S/S SECTOR-62 GREEN BELT, NOIDA IN THE AREA OF EUDSD-II, NOIDA:- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | CARRIAGE OF NEW 11 KV V.C.B. INCOMING C.T.R. 600/300/5A (01 NO.) AND 11 KV V.C.B. OUTGOING C.T.R. 400/200/5A (05 NOS.) FROM GHAZIABAD/ SHAHIBABAD/NOIDA/JE STORE TO SITE OF WORK WITH SAFE LOADING AND UNLOADING AT BOTH ENDS. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | LABOUR CHARGES FOR REPLACEMENT OF 11 KV V.C.B. INCOMING C.T.R. 600/300/5A (01 NO.) AND 11 KV V.C.B. OUTGOING C.T.R. 400/200/5A (05 NOS.) WITH ALL ACCESSORIES AND ERRECTION OF ABOVE NEW 11 KV V.C.B. INCOMING C.T.R. 600/300/5A (01 NO.) AND 11 KV V.C.B. OUTGOING C.T.R. 400/200/5A (05 NOS.) WITH REMOVING AND RECONNECTING 11 KV INCOMING AND OUTGOING CABLES, REMOVING AND REFIXING OF EARTHING AND WIRING AS REQUIRED IN VCB, ALL TESTING OF NEW VCB ETC WITH PROPER SAFETY TO COMPLETE THE WORK ETC IN ALL RESPECT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.03 | CARRIAGE OF DAMAGED & NON REPAIRABLE 11 KV V.C.B. INCOMING C.T.R. 600/300/5A (01 NO.) AND 11 KV V.C.B. OUTGOING C.T.R. 400/200/5A (05 NOS.) WITH ALL ACCESSORIES FROM SUB-STATION TO ELECTRICITY STORE WITH SAFE LOADING AND UNLOADING AT BOTH ENDS. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | PROVIDING AND INSTALLATION OF CHEMICAL EARTHING FOR NEW VCB BRAKER (WITH ALL MATERIAL AND LABOUR) AFTER INSTALLATION RESISTANCE SHOULD BE LESS THAN ONE OHM. AS PER FOLLOWING :- Note :- The all material and labour shall be provided by the contractor with 12 month guarantee for resistance value less than one OHM and should be checked 06 months after proper installation. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.01 | Providing of earth elctrode for chemical earthing Pipe in pipe type proper hot deep galvanization dia 80 mm length 3 mtr - 50mm x 6mm terminal connection hole dia 8mm The cavity between the pipe & pipe is filled with conductive mixture - for hermetically filling inside the cavity i.e. between secondary conductor & primary conductor, crystalline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc the electrode should be sealed from both the ends. The outer pipe of the elctrode should be galavanized the characteristics of this compound is highly cnductive, non magnetic & non corrosive in G.I. Including providing of backfill compound each elctrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested for new 11 KV VCB Braker. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.02 | Providing and fixing of GI strip of size 50 mm x 6 mm suitable for new 11 KV VCB Braker. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.03 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information