## BoQ1 (hidden)
Item Wise BoQ
BoQ_Ver3.0 | Item Wise | Normal | INR Only | INR
Select, Excess (+), Less (-)
Tender Inviting Authority: Executive Engineer, Electricity Construction & Works Division, Ghaziabad | [54 empty] | Bought Out
Name of Work:-Works at proposed Replacement of 33KV 3x300Sq.mm Damaged cable of 33KV line Koyal Enclave from Karan Gate, to near water supply pipe Double Pole Riser, Gzb. | [54 empty] | Direct
Tender Reference No : 33/ECWD/Gzb/2023-24 | [54 empty] | Quote for Supply Portion only
Bidder Name : | [54 empty] | Quote for Erection Portion only
PRICE BID 1. This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns after validating the sheet, else the bidder is liable to be rejected for this tender. 2. Bidders are allowed to enter the Bidder Name and Unit Ex-Works Price and GST in %age only. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents. 9. BIDDERS MUST FILLED UP THE GST IN %AGE OTHERWISE G.S.T. RATES WILL BE TREATED AS INCLUDED IN THE GIVEN BASIC RATES.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Description of Works | Item Code | Tendered Quantity | Unit | Estimated Rate | Bought-out /Direct | Specify Bought-out /Direct | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Ex-Works Price (Rs./Unit) | Excise Duty (Rs/Unit) | CST/VAT (Rs/Unit) | Other Taxes & Duties (Rs/Unit) | Freight & Insurance Charges (in Rs./Unit) |  |  | Unit FOR Dest. Supply Price incl. all Taxes and Duties (in Rs./Unit) (F+G+H+I+J) | Total Value for work (In Rs.) (C x F) | GST (in %age) | Total Value for GST (in Rs.) |  |  | Total Unit Price incl. GST (in Rs.) | [26 empty] | Total Amount excl. GST (in Rs.) | Total Amount incl. GST (in Rs.) | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | G.I. Channel 100x50x6 mm, 2400 mm long (9.56kg/mt) with G.I.Clamp of 65x8mm for dropper channel of 33KV line double pole/four pole | item1 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [8 empty] | 18 |  | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2 | Heat Shrinkable outdoor type end termination cable jointing kit suitable for 33KV XLPE 3x300 Sq. mm.cable | item2 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
3 | Heat Shrinkable straight through cable jointing kit suitable for 33KV XLPE 3x300 Sq. mm.cable | item3 | 2 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
4 | Carriage of following material from PVVNL store Cable H.T.XLPE 33KV 3x300SQ.M.M | item4 | 410 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
5 | 33KV composite Polymeric Pin insulator. | item5 | 3 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
6 | Erection of Following Material & Miscellaneous Electrical Works. Making Jumpers on Sectional Pole, by providing & fixing of P.G.Clamps of proper sizes, G.I.Nut Bolts & Washers suitable for Dog Conductor/ 33KV, 3x300Sq.mm XLPE cable. Existing End Double Pole | item6 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
7 | Existing Riser Double Pole | item7 | 1 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
8 | Making H.T.Connection of the proposed line from 33KV Line. The work consists of fixing & fabrication of Dropper Channels, & fixing of Disc Insulators, Pin Insulators, jumpering with P.G.Clamps, clamping and binding etc,as per site conditions. | item8 | 1 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
9 | Digging of Trench by excavation of earth of 1050x500mm size for 33KV line | item9 | 40 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
10 | Safe laying of 33KV, 3x300Sq.mm. XLPE Cable in Cable Trench to respective Double Pole. | item10 | 40 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
11 | Providing & Laying of Ist Class Bricks, along the length on both side of 33KV XLPE Cable in Cable Trench (minium 18No. Bricks/Mtr per Cable) and Stone Slab (Smooth surface both side) of size 400x600x40mm on top of the Cable, Providing 150mm thickness River sand for cushion beneath and 150mm above the cable as per specification. | item11 | 40 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
12 | Back filling of excavated earth in the cable trench upto the ground level and ramming properly. | item12 | 40 | Rmt. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
13 | Supply & Laying of HDPE Pipe PE-80, PN-6, DN-160mm dia by HDD trenchless method, as per site requirement. | item13 | 330 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
14 | Laying of 33KV, 3x300Sq.mm XLPE cable in HDPE Pipe PE-80, PN-6, DN-160mm dia by HDD trenchless method, as per site requirement. | item14 | 330 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
15 | Laying of 33KV, 3x300Sq.mm XLPE Cable in the air on cable Riser Double Pole, existing cable trench, Pucca trench, nala x-ing & G.I.Pipe and making connection with 33KV over head line at both ends. | item15 | 40 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
16 | Providing & Fixing 150mm dia 2mm thick 3M long G.I.Pipe over 33KV, 3x300Sq.mm XLPE Cable before mounting the 2No. Cable on double pole / Cable support structure. The work includes fixing of Clamp, sealing of top and bottom end of the G.I.Pipe. One end of G.I.Pipe is to be buried under earth about 500mm. | item16 | 4 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
17 | Making of 33KV Outdoor type cable end termination by heat shrinkable XLPE Cable Jointing Kits and crimping with proper size aluminium lugs. Work includes providing Aluminum lugs, insulating tapes etc as per specifications. | item17 | 4 | No. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
18 | Making of 33KV Straight through Cable Jointing Kits 3x300mm² and crimping of proper size aluminium lugs. Work includes providing insulating tapes etc as per specifications. | item18 | 2 | Mtr. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
19 | Supply & fixing of cable route marker along the route of 33KV cable with proper grouted with proper painting & marking PVVNL, 33KV HT Cable. | item19 | 5 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
20 | Road restoration charges for 1Mtr wide Kuccha Road (Inter locking Tiles, Bricks Road & Developed green belt only) or Deposite charges to take the permission/approval/NOC from any Development Authority/Govt. Body/Forest Deptt./and other concerned Deptt. for restoration of damaged property like Kuccha road, Inter locking Tiles and other utilities. | item20 | 20 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
21 | Road restoration charges for 1Mtr wide Pucca Road (Cemented, Concrete & Black road only) or Deposite charges to take the permission/approval/NOC from any Development Authority/Govt. Body/Forest Deptt./and other concerned Deptt. for restoration of damaged property like Pucca road, Inter locking Tiles and other utilities. | item21 | 300 | Mtr | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
22 | Cartage of empty cable drum from site to PVVNL store including loading & unloading at both ends respectively. | item22 | 1 | No. | 1 |  |  | Excess(+) |  | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
Total in Figures | [51 empty] | 0 | 0 |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [7 empty] | % | [39 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information