## BoQ1 (hidden)
Item Wise BoQ
BoQ_Ver3.0 | Item Wise | Normal | INR Only | INR
Select, Excess (+), Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Workshop Circle, Meerut | [54 empty] | Bought Out
Name of Work: (i) Supply of Gasket Set made of best quality Rubberized cork sheet RC-70C Conforming to IS 4253/Part-2/2008 with its latest amendment if any) for use in repairing of 25 KVA to 100 KVA Distribution Transformers) and as per specification, approved GTP and Drawing.(ii) Supply of Neoprene Oil Seals of different sizes suitable for Transformer made of best quality Neoprene Rubber as per relevant ISS meant for Electrical use in repairing of Distribution Transformer & as per approved Drawing & G.T.P | [54 empty] | Direct
Tender Reference No : S.T. E- T.No. 54/E. Workshop C./MRT/ 2023-24 | [54 empty] | Quote for Supply Portion only
Bidder Name : | [54 empty] | Quote for Erection Portion only
PRICE BID 1. This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns after validating the sheet, else the bidder is liable to be rejected for this tender. 2. Bidders are allowed to enter the Bidder Name and Unit Ex-Works Price and GST in %age only. 3. Above Schedule Structure and quantities is provisional and may vary as per site requirement. 4. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 5.Supply order/Contract will be awarded on basis L-1 Rates of Tendered items of the tender (in Condition Tendered material item is not a sub part of other tendered item) on the discretion of SE, EWC, Meerut. 6. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents. 7. Bidders must be filled up the GST in %age, Otherwise G.S.T. rates will be included in the given basic rates.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Description of Works | Item Code | Tendered Quantity | Unit | Estimated Rate | Bought-out /Direct | Specify Bought-out /Direct | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | Unit Ex-Works Price (Rs./unit) | Excise Duty (Rs/Unit) | CST/VAT (Rs/Unit) | Other Taxes & Duties (Rs/Unit) | Freight & Insurance Charges (in Rs./Unit) |  |  | Unit FOR Dest. Supply Price incl. all Taxes and Duties (in Rs./Unit) (F+G+H+I+J) | Total Value for work (In Rs.) (C x F) | GST (in %age) | Total Value for GST (in Rs.) (13*22/100) |  |  | Total Unit Price incl. GST (in Rs.) (13+23) | [26 empty] | Total Amount excl. GST (in Rs.) (4 x 13) | Total Amount incl. GST (in Rs.) (4 x 26) | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Supply of Gasket Set made of best quality Rubberized cork sheet RC-70C Conforming to IS 4253/Part-2/2008 with its latest amendment if any) for use in repairing of 25 KVA to 100 KVA Distribution Transformers) and as per specification, approved GTP and Drawing. Each Gasket set Consists of Gasket Washer as per following Detail & as per Sample. (a) Gasket Washer size Dia OD 110 mm, ID 75 mm, Thickness 6mm, - 03 Nos. (b) Gasket Washer size Dia OD 50 mm, ID 28mm, Thickness 6 mm - 12 Nos. (c) Gasket Washer size Dia OD 32 mm, ID 12 mm, Thickness 6mm - 04 Nos. Total 19 nos. washer pieces in one set & as per sample and enclosed Drg.Each set will be packed in Environmental friendly poly bag. (Tolerance in size +/- 0.25 mm, Negative Tolerance in Thickness is not allowed) | item5 | 60000 | Sets | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2 | Supply of Neoprene Oil Seals of following sizes suitable Transformer made of best quality Neoprene Rubber as per relevant ISS meant for Electrical use in repairing of Distribution Transformer & as per approved Drawing & G.T.P with following Properties:- (i) Shore Hardness - 38 to 42 Durometer A (ii) Tensile Strength - 105 Kg/cm2 (minimum) (iii) Ultimate elongation - 350% ( minimum) (iv) Size tolerance Radius - (+/-) 1.0 mm (v) Height & other Dimension- (+) 0 mm, (-) 1.0 mm
2.01 | in size M-12 suitable for LT side Transformer | item6 | 100000 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2.02 | in size M-12 suitable for H.T Side of Transformer | item7 | 100000 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
2.03 | in size M-20 suitable for L.T side of Transformer | item8 | 10000 | Nos. | 1 |  |  | Excess(+) | 1 | Full Conversion | INR | [10 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 | #VALUE!
Total in Figures | [21 empty] | 0 |  |  | 0 | [26 empty] | 0 | 0 |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [7 empty] | % | [39 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information