## P V V N L-MT/COM/12(s)/22-23

TECHNICAL SPECIFICATION FOR 33 KV CTs (SINGLE PHASE)

- GENERAL:

  - This specification covers the design, manufacturing, testing and supply of 33 KV CTs

1.2       CTs shall comply with the requirements of the relevant I.S. specifications.

  - List of raw material to be used along with name of suppliers should be submitted with the tender.

2.1      The firm should have valid type test report of the offered equipment as elaborated in the relevant clause of PQR, as per relevant ISS and/or any other specified international standards during the last 5-year period issued from ERDA/NTHM/ CPRI. Photocopy of such type test reports/ certificates must be submitted along with tender bid. The type test certificates of prototype manufactured and tested by foreign collaborators of the tenderer at their works shall not be acceptable for indigenously manufactured equipment.

  - If the firms are meeting other eligibility requirement of the tender but do not have valid type test report as per current technical specification with revised parameters as prescribed by PVVNL for cross sectional area of conductor, core, current density, the firm shall have to give undertaking to submit valid type test report of offered equipment issued by CPRI/ERDA only within maximum period of three months time. Keeping in view of the timely completion of projects supplies shall be accepted with the provision that 80% payment shall only be released and the balance 20% may be released only after submission of valid type test report.

3.0	ELECTRICAL COMPONENTS:

The supplier shall be original manufacturer of the epoxy resin cast CT or accredited representative of such manufacturer. The bidder must have facility to cast epoxy resin by hot casting process under vacuum for CTs at his own works. These CTs should have been type tested as per relevant ISS (latest revision) in a Govt. accredited National Test House such as CPRI, Bangalore / Bhopal etc. during the last five years from the date of Tender opening. A brief detail of the various components to be provided in the metering cubicle is give below:-

3.1	CURRENT TRANSFORMERS:

There shall be Single Core single ratio dry type epoxy resin cast current Transformers as per IS: 2705: 1992 of latest revisions thereof as per details mentioned below:-

TYPE: Dry type epoxy Resin cast CTs.

Capacity		10/1A,15/1A,20/1A,25/1A,30/1A,40/1A, 50/1A,60/1A,70/1A, 75/1A, 100/1A, 200/1A or higher ratios as per the requirement of PVVNL

(a)	Rated Voltage		33KV

(b)	No. of cores		One

(c) 	Rated VA Output	`	2.5 VA

(d)	Rated continuous Thermal		As per IS: 2705: 1992

Current temperature rises over ambient.

(e)	One minute withstand Power		As per ISS

frequency voltage (for primary

and secondary)

Class of accuracy		    0.5  S.

(f) Current density at rated current(Max)	    1.5 Amp. Per sq. mm

(g) Current density at STC for 1 second(max)	    165 Amp. Per sq. mm

(h) Cross sectional area of primary as per current   Should be as per  rated current density    density			      or as per current density at STC			     (for 1 second) whichever is higher.

(i) Short time thermal current rating	   	              10/1 to 20/1-7.8KA for 0.5 sec

25/1 to 40/1-7.8 KA for 1.0 sec

50/1 to 250/1-13.0 KA for 1.0 sec etc as per relevant IS

| (j). | Rated dynamic current rating |  | 2.5 times of short time thermal current rating |
| --- | --- | --- | --- |
| (k) | Rated continuous thermal current |  | 1.2 times of rated primary current |
| (l). | Instrument Security factor |  | < 5 |
| (m). | All other characteristics and test parameter |  | As per IS: 2705/1992 (latest version) |
| (n). | Max temperature rise over ambient temp of 50º at rated continuous thermal current at rated frequency rated bush. |  | 45ºc |

Material

(i)	Core	High-grade non-ageing electrical low

loss core of superior CRGO silicon

sheet steel.

(ii)	Conductor	Super enameled copper wire

(iii)	Insulation	Resin cast.

(iv)	Base 	MS Hot dip galvanized.

Secondary Termination	From and effective Termination S 1& S2

shall be clearly marked.

Fault Level	13.1. KA for 1 Sec

The current transformer should have been type tested and routine tested as per IS: 2705/1992 or latest amendment thereof.

3.2	MAKE OF THE COMPONENT:

List of raw material to be used along with names of the suppliers should be submitted with Part-I & II of the tender. Make of various components as detailed above and as      being 	given below.

3.2.1	HARDWARE:

Hot-Dip Galvanized of any standard make.

3.2.2	PAINT:

Epoxy – Paint of standard make.

3.2.3    EPOXY RESIN: –

Dr. Beck, Huntsman, Atul.

4.0	INSPECTION AND TESTING:

All CTs shall be inspected and tested at manufacturer works to verify that these are being supplied in accordance with relevant standards. Technical Specification, Guaranteed Technical Particulars and acceptance and routine tests.

Inspection of material offered for inspection shall be carried out jointly by the representative of Superintending Engineer (DQC), PVVNL, Meerut.

While offering for inspection / testing confirming to the effect that the CTs have successfully withstand the routing tests (along with test results)  is required to be submitted for each lot offered for inspection to Superintending Engineer (DQC), PVVNL, Meerut.

All the instruments used in inspection and testing should be properly calibrated and sealed once a year. Calibration certificate when demanded by the inspecting officer shall be provided / produced for verification purpose. In case of any dispute regarding calibration, instruments shall be sealed and singed by the representative of the supplier and purchaser and will be sent to test house / Govt. Lab / Govt. institution of repute, for calibration at the cost of supplier. The result of such testing shall be binding on the supplier.

Purchaser reserves the right to get the components like CT's  etc. inspected / type tested before dispatch by any independent inspection agency at the cost of purchaser in case the equipment with stand the type test, otherwise the supplier has to bear such cost in addition to any other action deemed appropriate by the purchaser.

One sample of CT of any ratio randomly selected from each offered lot, shall be opened for verifying the diameter & cross sectional area of primary coil conductors including verification of GTP

Testing Facility: - The manufacturer must have testing facilities at their works as per clause No. 1.2.3 of "Instruction to Tenderer" to carry out all the routine & acceptance test (including partial discharge test) as mentioned below. List of Testing equipment with photo copy of calibration certificates should be enclosed with Part- I of the tender.

Schematic drawing showing each and every details, dimensions and wiring diagrams shall be submitted necessary for each type of metering cubicle.

4.1	Type test:

All the type tests as listed below shall be carried out for the equipment strictly as described as per the relevant IS (or latest amendment thereafter).

4.1.1	Current Transformers (As per IS: 2705 / 1992 or its latest Amendment)

(A) Type Testing will be done on CT of any one ratio if-

(i)	The type tested CT has maximum dynamic AT’s in confirmation to IS:2705, 1992 Clause no. 9.6.2 (Notes)

(ii)	The shape size construction of all the ratio is same. However if shape size & construction varies for different ratio’s then all type test shall be repeated accordingly for each shape, size & construction.

a)	Short-time current test.

b)	High Voltage power frequency on primary windings.

c)	High Voltage power frequency on secondary windings.

d) 	Lightning impulse test

e)	Determination of error according to the requirements of appropriate accuracy class

f)	Temperature rise test on any one selected sample of each ratio.

g)	Partial discharge test

h)	Instruments security factor (ISF) test as per IS:2705. Part-II or any latest amendment.

4.2	Routine Tests: -

The following shall constitute the routine test and acceptance tests.

4.2.1 	Current Transformers

- Verification of terminal markings and polarity

- High Voltage power frequency test on primary windings.

- High voltage power frequency test on secondary windings.

- Over voltage inter turn test.

- Determination of error according to the requirements of appropriate accuracy class.

- Partial discharge test in accordance with IS: 11322 / 1985.

- Instruments security factor test(IFS) as per IS:2705.

4.3	Acceptance Test:

4.4	Current Transformers

- Verification of terminal markings and polarity

- High Voltage power frequency on primary windings.

- High Voltage power frequency on secondary windings.

- Determination of error according to the requirements of appropriate accuracy class

- Temperature rise test.

- Partial discharge test

- Instruments security factor test(IFS) as per IS:2705.

5.0	In case of any discrepancy between specification and relevant standard, provision 	contained in this specification shall prevail.