## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-II, Noida
Name of Work : fo¦qr uxjh; forj.k [k.M & f}rh;] uks,Mk ds vUrxZr 2ua0 33 dsoh ubZ ykbZu fuekZ.k ,oa lqn`<hdj.k dk dk;ZA
Contract No: SHORT TERM E-TENDER NO 166/EUDC-II NOIDA/2023-24
G.S.T. AND ALL TAXES INCLUSIVE IN ALL QUOATED RATES.
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) (Note:- Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC.) The rate quoted by the tenderer shall be inclusive of all duties, taxes (except GST), fees, octroi and other levies, materials, any type of NOC, labour to & FOR transportation of material and labour charges etc. GST AND ALL TAXES INCLUSIVE IN QUOTED RATES. 3. The entire work is to be done on 'Departmental' basis. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE per unit In Figures To be entered by the Bidder INCLUSIVE OF ALL TAXES AND GST Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT with All Taxes and GST in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | 33@11 ds0oh0 fo¦qr midsUnz lSDVj&80 iqjkuk uks,Mk ds vfrfjDr lkslZ gsrq fyaDM+ ykbZu ds fuekZ.k dk dk;Z ftls 132@33 ds0oh0 fo¦qr midsUnz Hkaxsy uks,Mk ls iksf"kr iks"kd la0&06@07 ls tksMdj fo¦qr vkiwfrZ djus dk dk;ZA | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Safe carriage of following stock material, from any of the Store Center of PVVNL to work site including Loading from Store and safe unloading at site for Item No. 3 to 14 | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | ST/PCC 11 Mtr long Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 43 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | 33KV 3X300SQMM XLPE CABLE |  | 1 | Mtr. | 100 |  |  | Excess(+) | 380 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | ACSR Dog Conductor |  | 1 | Mtr. | 100 |  |  | Excess(+) | 3850 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | 33KV V-Type Steel Cross Arm |  | 1 | Nos. | 100 |  |  | Excess(+) | 25 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | MS Channel 125x65x3200mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 9 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | MS Angle 75x75x6mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | 33KV Polymerice Disc Insulator with Fittings |  | 1 | Nos. | 100 |  |  | Excess(+) | 86 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | 33KV Polymerice Pin Insulator with Pin. |  | 1 | Nos. | 100 |  |  | Excess(+) | 84 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | 33KV X Arm |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | Stay set complete (G.I.Stay rod 16x1800mm, Stay wire 5Kg, Guy insulator, G.I.Stay clamp, bolt, nut & wasther with concrete grouting) for 11KV line. |  | 1 | Set | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | Heat Shrinkable outdoor type end termination cable jointing kit suitable for 33KV XLPE 3x300 Sq.mm. cable (Make - Raychem/3M/Denson) |  | 1 | Nos. | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | Heat Shrinkable Straight Through Box suitable for 33KV XLPE 3x300 Sq.mm. cable (Make - Raychem/3M/Denson) |  | 1 | Nos. | 100 |  |  | Excess(+) | 24 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | Errection of above Following material and Supply and errection of the below material for completing the works as per RESPO. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 65x8mm, G.I.Nut bolt & washer, P.G.Clamp, Stone Pad, Al. Binding wire, 'E' bracket 75x10mm, and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as any fabrication work if required & fixing of cross bracing sets 4.3mtr long, from G.I.Angle 65x65x6mm. The work includes cutting holes and providing G.I.Bolt of 16x40mm size, in the middle of the cross bracing with 01No. spring washer of proper size as per drawing/ as per schedule. Double Pole Structures (a) ST/PCC - 11 Mtr. Long Pole |  | 1 | Nos | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 'F' bracket 75x10mm, G.I.Nut bolt & washer, Stone Pad Al. Binding wire and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as an fabrication work if required. Single Pole (a) ST/PCC - 11 Mtr. Long Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 27 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Grouting of supports in CC 1:3:6 (Cement, sand & 20mm stone grift). Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, upto ground level, 300mm plinth above the ground level with C.C. 1:3:6 (Cement, Course sand and Stone grift) with muffing as per RESPO. Work includes back filling and proper ramming. Single Pole and Double Pole (a) ST/PCC - 11 Mtr. Long Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 43 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | Laying, spreading, lifting and final sagging of 3 phases ACSR Dog conductor in accordance with Line chart includidng binding and fixing of all accessories in 03Nos. Conductor in parallel as per site requirement. |  | 1 | Mtr | 100 |  |  | Excess(+) | 3850 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | FIXING OF PIN INSULATOR WITH PIN, COMPLETE WORK IN ALL RESPECT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 84 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | FIXING OF Disc. INSULATOR WITH Fitting, COMPLETE WORK IN ALL RESPECT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 86 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | FIXING OF MS CHANNEL AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 9 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
23 | FIXING OF MS ANGLE AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
24 | Fixing, tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing, including providing & fixing of Stay Insulators of 11KV and Stay Clamps and Grouting of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:3:6 cement, sand, 20mm Stone grift) as per drg. Including back filling of soil and proper ramming etc. |  | 1 | Set | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | FIXING OF 33KV V-Type Steel Cross Arm with COMPLETE WORK IN ALL RESPECT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 25 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
26 | FIXING OF 33KV X Arms with COMPLETE WORK IN ALL RESPECT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | Preparation of 33 KV Power Cable ends: Making of 33 KV XLPE Heat shrinkable outdoor jointing kits suitable for 3x300sqmm XLPE Cable after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs with complete connention in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
28 | Laying and commissiong of 33KV 3x300sqmm XLPE Cable Double Ckt. after digging trench of dia 220 mm in two parallel bores for Double Curcuit by manual method at a depth of 1.50 mtrs to 2.50 mtrs. (as requirement at site) below the ground level for laying cable and refilling of trench including connections at both ends after providing and crimping of lugs of proper size for completion of work and Providing & Laying of Ist Class Bricks, along the length on both side of 11KV XLPE Cable in Cable Trench (minium 18No. Bricks/Mtr per Cable) and Stone Slab of size 450x600x50mm on top of the each Cable, Providing 150 thickness mm River sand for cushion beneath and 150mm above the cable and Back filling of excavated earth in the cable trench upto the ground level and ramming properly. |  | 1 | Mtr | 100 |  |  | Excess(+) | 250 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
29 | Laying of 33 KV 3X300 Sq.mm XLPE Cable in the air on cable Riser Double Pole, existing trench cable trench, nala x-ing & G.I.Pipe and making connection complete at both ends. |  | 1 | Mtr | 100 |  |  | Excess(+) | 130 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
30 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop and making risers at double pole and re-filling of pits in proper manner with required material at kacha/pakka and hot mix road. (All Work and material in the scope of contractor) |  | 1 | Job | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
31 | PROVIDING AND FIXING OF NUT, BOLT AND WASHERS AS PER REQUIREMENT. |  | 1 | Kg. | 100 |  |  | Excess(+) | 60 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
32 | Tree Cutting and Chopping in the areas of above line. (All work in the scope of contractor.) |  | 1 | Span | 100 |  |  | Excess(+) | 20 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
33 | Providing and Driving of MS earth rod of size 20x2500 mm in earth and jointing through G.I. wire of 6 SWG between support and earth electrode by providing proper size of bolts and nuts for pole earthing. Supply Erection, fixing, grouting of stay rod in cement, sand and brick ballast in ration 1:4:8 in Block 600*600*300 mm with binding & nuzzling including providing & fixing of stay insulator complete in all respect with grouting. (All Work and Material in the scope of Contractor) |  | 1 | Nos | 100 |  |  | Excess(+) | 25 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
34 | Repairing of H.V. 33 KV Underground cable faults in various voltage level cables on Turnkey Basis (Providing and its Commissioning New Technology Fault Locator Machine with Driver, and other material related to work etc.) in the areas of SDO -V, Noida. The Contractor shall be responsible for providing the Cable Fault Locating Machines of appropriate and latest version & specifications along with experienced technician, helpers and driver etc. by their own end for locating the 33 KV Cable Fault in the above SDO areas and Pin pointing within two meter of cable fault, exposing the same in the underground HT cable (33 KV) including cutting of the Faulty Cable, its meggering & sealing of healthy cable. In addition to locating and pin pointing of cable faults, the contractor shall also be responsible for digging of cable trench of suitable size so as to enable making of cable joints (one or two straight through joints depending on the requirements), it shall also include cutting of the faulty cable in sufficient length. Road cutting & digging thereof so that cable may be taken out for jointing work. Dressing of road as may be required at various places. as per Following : | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
35 | 33 KV cable fault location & trench digging with the help road cutter/digging machine/tractor etc. as per site requirement (size of trench 4 m length & 1.5 m width) in SDO -V, Noida areas. |  | 1 | Job | 100 |  |  | Excess(+) | 24 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
36 | Fixing, Making and commissioning of 33 KV Straight through with the help of Jointer per 33 KV joint for filling with complete connections in all respect. (33 KV 3x300/400 Sq.mm. Outdoor, Indoor jointing Kits and Straight through of Raychem/ 3M/ Denson make and Jointer provided by the contractor. and Replacement of 33 KV damaged cable in trench after making joint and filling of sand/brick/soil as per site requirement. |  | 1 | Job | 100 |  |  | Excess(+) | 24 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
37 | 33@11 ds0oh0 fo¦qr midsUnz lSDVj&80 u;k uks,Mk ds vfrfjDr lkslZ gsrq fyaDM+ ykbZu ds fuekZ.k dk dk;Z ftls 132@33 ds0oh0 fo¦qr midsUnz Hkaxsy uks,Mk ls iksf"kr iks"kd la0&06@07 ls tksMdj fo¦qr vkiwfrz djus dk dk;ZA | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
38 | Safe carriage of following stock material, from any of the Store Center of PVVNL to work site including Loading from Store and safe unloading at site for Item No. 39 to 50 | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
39 | ST/PCC 11 Mtr long Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 56 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
40 | 33KV 3X300SQMM XLPE CABLE |  | 1 | Mtr. | 100 |  |  | Excess(+) | 550 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
41 | ACSR Dog Conductor |  | 1 | Mtr. | 100 |  |  | Excess(+) | 1880 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
42 | 33KV V-Type Steel Cross Arm |  | 1 | Nos. | 100 |  |  | Excess(+) | 35 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
43 | MS Channel 125x65x3200mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
44 | MS Angle 75x75x6mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
45 | 33KV Polymerice Disc Insulator with Fittings |  | 1 | Nos. | 100 |  |  | Excess(+) | 48 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
46 | 33KV Polymerice Pin Insulator with Pin. |  | 1 | Nos. | 100 |  |  | Excess(+) | 180 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
47 | 33KV X Arm |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
48 | Stay set complete (G.I.Stay rod 16x1800mm, Stay wire 5Kg, Guy insulator, G.I.Stay clamp, bolt, nut & wasther with concrete grouting) for 11KV line. |  | 1 | Set | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
49 | Heat Shrinkable outdoor type end termination cable jointing kit suitable for 33KV XLPE 3x300 Sq.mm. cable (Make - Raychem/3M/Denson) |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
50 | Heat Shrinkable Straight Through Box suitable for 33KV XLPE 3x300 Sq.mm. cable (Make - Raychem/3M/Denson) |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
51 | Errection of above Following material and Supply and errection of the below material for completing the works as per RESPO. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
52 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 65x8mm, G.I.Nut bolt & washer, P.G.Clamp, Stone Pad, Al. Binding wire, 'E' bracket 75x10mm, and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as any fabrication work if required & fixing of cross bracing sets 4.3mtr long, from G.I.Angle 65x65x6mm. The work includes cutting holes and providing G.I.Bolt of 16x40mm size, in the middle of the cross bracing with 01No. spring washer of proper size as per drawing/ as per schedule. Double Pole Structures (a) ST/PCC - 11 Mtr. Long Pole |  | 1 | Nos | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
53 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 'F' bracket 75x10mm, G.I.Nut bolt & washer, Stone Pad Al. Binding wire and other accessories as per drawing. The work includes carriage and handling of supports from sectional store to pit site as well as an fabrication work if required. Single Pole (a) ST/PCC - 11 Mtr. Long Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 48 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
54 | Grouting of supports in CC 1:3:6 (Cement, sand & 20mm stone grift). Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, upto ground level, 300mm plinth above the ground level with C.C. 1:3:6 (Cement, Course sand and Stone grift) with muffing as per RESPO. Work includes back filling and proper ramming. Single Pole and Double Pole (a) ST/PCC - 11 Mtr. Long Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 56 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
55 | Laying, spreading, lifting and final sagging of 3 phases ACSR Dog conductor in accordance with Line chart includidng binding and fixing of all accessories in 03Nos. Conductor in parallel as per site requirement. |  | 1 | Mtr | 100 |  |  | Excess(+) | 1880 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
56 | FIXING OF PIN INSULATOR WITH PIN, COMPLETE WORK IN ALL RESPECT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 180 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
57 | FIXING OF Disc. INSULATOR WITH Fitting, COMPLETE WORK IN ALL RESPECT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 48 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
58 | FIXING OF MS CHANNEL AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
59 | FIXING OF MS ANGLE AS PER SITE REQUIREMENT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
60 | Fixing, tightening & nozzling of stay wire with stay rod with the poles of required tension as per drawing, including providing & fixing of Stay Insulators of 11KV and Stay Clamps and Grouting of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:3:6 cement, sand, 20mm Stone grift) as per drg. Including back filling of soil and proper ramming etc. |  | 1 | Set | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
61 | FIXING OF 33KV V-Type Steel Cross Arm with COMPLETE WORK IN ALL RESPECT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 35 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
62 | FIXING OF 33KV X Arms with COMPLETE WORK IN ALL RESPECT. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
63 | Preparation of 33 KV Power Cable ends: Making of 33 KV XLPE Heat shrinkable outdoor jointing kits suitable for 3x300sqmm XLPE Cable after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs with complete connention in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
64 | Laying and commissiong of 33KV 3x300sqmm XLPE Cable Double Ckt. after digging trench of dia 220 mm in two parallel bores for Double Curcuit by manual method at a depth of 1.50 mtrs to 2.50 mtrs. (as requirement at site) below the ground level for laying cable and refilling of trench including connections at both ends after providing and crimping of lugs of proper size for completion of work and Providing & Laying of Ist Class Bricks, along the length on both side of 11KV XLPE Cable in Cable Trench (minium 18No. Bricks/Mtr per Cable) and Stone Slab of size 450x600x50mm on top of the each Cable, Providing 150 thickness mm River sand for cushion beneath and 150mm above the cable and Back filling of excavated earth in the cable trench upto the ground level and ramming properly. |  | 1 | Mtr | 100 |  |  | Excess(+) | 410 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
65 | Laying of 33 KV 3X300 Sq.mm XLPE Cable in the air on cable Riser Double Pole, existing trench cable trench, nala x-ing & G.I.Pipe and making connection complete at both ends. |  | 1 | Mtr | 100 |  |  | Excess(+) | 140 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
66 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop and making risers at double pole and re-filling of pits in proper manner with required material at kacha/pakka and hot mix road. (All Work and material in the scope of contractor) |  | 1 | Job | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
67 | PROVIDING AND FIXING OF NUT, BOLT AND WASHERS AS PER REQUIREMENT. |  | 1 | Kg. | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
68 | Tree Cutting and Chopping in the areas of above line. (All work in the scope of contractor.) |  | 1 | Span | 100 |  |  | Excess(+) | 120 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
69 | Providing and Driving of MS earth rod of size 20x2500 mm in earth and jointing through G.I. wire of 6 SWG between support and earth electrode by providing proper size of bolts and nuts for pole earthing. Supply Erection, fixing, grouting of stay rod in cement, sand and brick ballast in ration 1:4:8 in Block 600*600*300 mm with binding & nuzzling including providing & fixing of stay insulator complete in all respect with grouting. (All Work and Material in the scope of Contractor) |  | 1 | Nos | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
70 | Repairing of H.V. 33 KV Underground cable faults in various voltage level cables on Turnkey Basis (Providing and its Commissioning New Technology Fault Locator Machine with Driver, and other material related to work etc.) in the areas of SDO -V, Noida. The Contractor shall be responsible for providing the Cable Fault Locating Machines of appropriate and latest version & specifications along with experienced technician, helpers and driver etc. by their own end for locating the 33 KV Cable Fault in the above SDO areas and Pin pointing within two meter of cable fault, exposing the same in the underground HT cable (33 KV) including cutting of the Faulty Cable, its meggering & sealing of healthy cable. In addition to locating and pin pointing of cable faults, the contractor shall also be responsible for digging of cable trench of suitable size so as to enable making of cable joints (one or two straight through joints depending on the requirements), it shall also include cutting of the faulty cable in sufficient length. Road cutting & digging thereof so that cable may be taken out for jointing work. Dressing of road as may be required at various places. as per Following : | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
71 | 33 KV cable fault location & trench digging with the help road cutter/digging machine/tractor etc. as per site requirement (size of trench 4 m length & 1.5 m width) in SDO -V, Noida areas. |  | 1 | Job | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
72 | Fixing, Making and commissioning of 33 KV Straight through with the help of Jointer per 33 KV joint for filling with complete connections in all respect. (33 KV 3x300/400 Sq.mm. Outdoor, Indoor jointing Kits and Straight through of Raychem/ 3M/ Denson make and Jointer provided by the contractor. and Replacement of 33 KV damaged cable in trench after making joint and filling of sand/brick/soil as per site requirement. |  | 1 | Job | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information