## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, Electricity Distribution Circle-I Muzaffarnagar
Name of Work: Under the work area of Executive Engineer, Electricity Distribution Division-I, Muzaffarnagar Subordinate Subdivision Officer, Electricity Distribution Subdivision-III, Muzaffarnagar under the Additional Business Plan 2024-25, Installation of 02 RMUs to eliminate the problem of power disruption of 04 nos. 11 kV industrial feeders emanating from 33/11 KV substation MAKHIYALI, the work of construction should be done through external agency.
Contract No: 48/2024-25/EDC-I/MZN
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only)
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Excluding GST | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 5 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 6 | 54 | 7
1 | The work of delivering following material from the Departmental store center to the site in which includes loading and unloading on both sides. (distance 0 to 50 km) | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | 11 KV XLPE CABLE 3x185 Sqmm |  | 250 | Mtr. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.02 | 11 KV CABLE OUTDOOR JOINTING KIT 3x185 Sqmm |  | 4 | No | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.03 | 11 KV CABLE INDOOR JOINTING KIT 3x185 Sqmm |  | 4 | No | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2 | Complete work of installing the electrical material received from the store center at the site. | [53 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
2.01 | Supply & fixing of 12kv 630 Amps 21KA for 3Sec. SF6 , BIL 28 KV/75 KV peak, extensible, outdoor duty 3-way, fully motorised and manually operated Ring Mains Unit originally manufactured byOEM in its factory only, comprising of one load break switch and 1 vaccum circuit breaker consisting of copper busbar in SF6 insulated tank with a provision electromechanical interlok to avoid accidental closure of earthing switch even when cable is in live condition. RMU should be Type Tested for internal arc of 21 KA for 1 Sec with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personal. Suitable Ct 200-50/1 A with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot for termination Kits. All the necessary wirings and Dummy panel/space for FRTU to be given along with RMU for future compatibility with SCADA system (Supply of FRTU is not in scope). Battery Charger etc. for Motorised Operation of RMU to be provided. The scope is including Plinth/ Angle iron Stand as per OEM design complete in all respect as per the direction of Engineer incharge. Complete RMU and its accessories should be suitable for altitude of 100 mtr above Sea Level. (ISI High Standard). complete in all respect. All necessary decentralized materials will be provide by the contractor / Firm. |  | 2 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.02 | Providing of earth electrode for chemical earthing Pipe in pipe type proper hot dip Galvanization dia 50 mm lenth 3 mtr - 32mm x6mm terminal connection hole dia 8mm The cavity between the pipe & Pipe is filled with conductive Mixture - for hermetically Filling inside the cavity i.e. between secondary conductor & Primary conductor, crystalline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc. The electrode should be sealed from both the ends. The outer pipe of the electrode should be galvanized the characteristics of this compound is highly conductive, nonmagnetic & noncorrosive in G.I. Including providing of backfill compound. Each electrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested for RMUs installed at above 33/11 KV Substations MAKHIYALI. All necessary decentralized materials will be provide by the contractor / Firm. |  | 2 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.03 | Complete work of Laying/ Installation 11 KV XLPE CABLE 3x185 Sqmm at 33/11 KV sub-station MAKHIYALI. as per RESPO standards. In which necessary Decentralized materials will be provide by the contractor / Firm. |  | 250 | Mtr. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.04 | Complete work of Installing and Commissioning of 11 KV CABLE JOINTING KIT INDOOR 3x300 Sqmm as per RESPO standards. All necessary decentralized materials will be provide by the contractor / Firm. |  | 4 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.05 | Complete work of Installing and Commissioning of 11 KV CABLE JOINTING KIT OUTDOOR 3x300 Sqmm as per RESPO standards. All necessary decentralized materials will be provide by the contractor / Firm. |  | 4 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.06 | Complete work of Fencing of Established RMU, at 33/11 KV substation MAKHIYALI. as per RESPO standards. All necessary decentralized materials will be provide by the contractor / Firm. |  | 2 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information