## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-II, Noida
Name of Work :fctusl Iyku 2025&26 ds vUrZxr fo¦qr uxjh; forj.k e.My & f}rh;] uks,Mk ds {ks= 11@0-4 dsoh midsUnzksa dh {kerko`f) en esa 50 ua0 vfrHkkfjr ifjorZdksa dh {kerko`f) djus ls lEcfU/kr dk;ZA
Contract No: SHORT TERM E-TENDER NO 32/EUDC-II NOIDA/2025-26
G.S.T. INCLUSIVE IN QUOTED RATES.
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) (Note:- Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC.) 2.The rate quoted by the tenderer shall be inclusive of all duties, taxes (INCLUSIVE OF GST), fees, octroi and other levies, materials, any type of NOC, labour to & FOR transportation of material and labour charges etc. ALL TAXES INCLUSIVE IN QUOTED RATES . 3. The work is to be done on SEMI TURNKEY BASIS. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE per unit In Figures To be entered by the Bidder with GST IN Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT with GST in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | fctusl Iyku 2025&26 ds vUrZxr fo¦qr uxjh; forj.k e.My & f}rh;] uks,Mk ds {ks= 11@0-4 dsoh midsUnzksa dh {kerko`f) en esa 50 ua0 vfrHkkfjr ifjorZdksa dh {kerko`f) djus ls lEcfU/kr dk;ZA | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Safe Cartage of following centralised stock material from any of the Store Center of PVVNL Discom to work site including Loading from Store and safe unloading at site for Item No. 3 to 21 | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | PCC Pole 11 Mtr Long |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | PCC Pole 8.5 Mtr Long |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | Stone Pad |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | ACSR Weasel Conductor |  | 1 | Mtr. | 100 |  |  | Excess(+) | 90 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | Dropper Channel |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | T Channel 125x65x1300 mm |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | Top Channel |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | Pin Insulator |  | 1 | Nos. | 100 |  |  | Excess(+) | 55 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | EARTHING |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | Disc Insulator |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | STAY SET |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | Connecting Lead 1x16 Sq mm |  | 1 | Mtr. | 100 |  |  | Excess(+) | 3356 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | 11 KV Fuse Set |  | 1 | Nos. | 100 |  |  | Excess(+) | 48 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | 11 KV Disc Fitting |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | LT PVC Cable Al 1x240 Sq mm |  | 1 | Mtr. | 100 |  |  | Excess(+) | 200 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | LT ABC (3x120+1x95+1x16) Sq mm |  | 1 | Mtr. | 100 |  |  | Excess(+) | 17930 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | LT XPLE CABLE ALU. 3.5X400SQMM |  | 1 | Mtr. | 100 |  |  | Excess(+) | 40 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | Distribution Box with clamp |  | 1 | Nos. | 100 |  |  | Excess(+) | 781 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | 250 KVA T/F |  | 1 | Nos. | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | Errection of above Centralised material and Supply and errection of the below De-Centralised material for completing the works as per RESPO. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
23 | Installation and Commissioning of 11/0.4 KV, 250 KVA T/F Mounted on Plinth as per site requirement and providing & fixing of Lugs & copper L-piece (04 No.) of size 400x50x6mm and making of L.T.Connections with complete work in all respects. |  | 1 | Job | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
24 | The excavation of foundation pit in mix soil/normal soil/soft soil & hard rock as per site condition and its back filling and leveling etc. The size of the pit will be (750x450)mm and having depth of 1/6th of the full length of the support. Erection of support, complete with providing & fixing of all G.I.Clamps size of 75x10mm, 65x8mm, G.I.Nut bolt & washer, P.G.Clamp, Stone Pad, Al. Binding wire, 'E' bracket 75x10mm, and other accessories as per RESPO. The work includes carriage and handling of supports from sectional store to pit site as well as any fabrication work if required & fixing of cross bracing sets 4.3mtr long, from G.I.Angle 65x65x6mm. The work includes cutting holes and providing G.I.Bolt of 16x40mm size, in the middle of the cross bracing with 01No. spring washer of proper size as per drawing/ as per schedule. Double Pole Structures (a) PCC/ST - 11 Mtr. Long Pole and 8.5 Mtr Lon |  | 1 | Nos. | 100 |  |  | Excess(+) | 5 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | Grouting of supports in CC 1:3:6 (Cement, sand & 20mm stone grift). Grouting will be done in the block of size (450x450)mm x1/6th of full length of the support, upto ground level, 300mm plinth above the ground level with C.C. 1:3:6 (Cement, Course sand and Stone grift) with muffing as per RESPO. Work includes back filling and proper ramming. Road Restoration charges shall be inclusive in quoted rates. Single Pole and Double Pole (a) 11M Long ST/PCC Pole |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
26 | Laying, Sagging and Re-Sagging of AB Cable 3x120sqmm at different locations of T/F as per site requirement. |  | 1 | Mtr | 100 |  |  | Excess(+) | 17930 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | Laying Fixing of LT XLPE Alu. Cable 3.5x400 sqmm at different locations of T/F as per site requirement. as per site requirement. |  | 1 | Mtr | 100 |  |  | Excess(+) | 781 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
28 | Installation and Fixing of 11 KV Fuse Set: Assembling and installation of fuse set on the fuse set structure of the T/F. The work includes fabrication for proper fixing, if required. Complete work in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 48 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
29 | Laying, spreading, lifting and final sagging of 3 OR 4 phases ACSR Weasel conductor in accordance with Line chart includidng binding and fixing of all accessories in 03Nos OR 04 Nos. Conductor in parallel as per site requirement. |  | 1 | Mtr | 100 |  |  | Excess(+) | 90 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
30 | Fixing of Stone Pad as per site requirement with complete work in all respect as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
31 | Fixing of Dropper channel as per site requirement with complete work in all respect as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
32 | Fixing of T channel as per site requirement with complete work in all respect as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
33 | Fixing, tightening & nozzling of stay wire with stay rod with the poles including providing & fixing of Stay Insulators of 11KV and Stay Clamps AND Grouting of stay rods (20x1800)mm including all work of excavation, cement concrete in size (0.60x0.60x0.30)m in ratio 1:3:6 cement, sand, 20mm Stone grift) as per drg. Including back filling of soil and proper ramming etc. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
34 | Fixing of Top channel as per site requirement with complete work in all respect as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
35 | Fixing of 11KV Disc Insulator with Fitting as per site requirement with complete work in all respect as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
36 | Fixing of 11KV Pin Insulator with Pin as per site requirement with complete work in all respect as per RESPO. |  | 1 | Nos. | 100 |  |  | Excess(+) | 55 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
37 | Driving of MS earth rod of size 20x2500 mm in earth and jointing through G.I. wire of 6 SWG between support and earth electrode by providing proper size of bolts and nuts for pole earthing. Supply Erection, fixing, grouting of stay rod in cement, sand and brick ballast in ration 1:4:8 in Block 600*600*300 mm with binding & nuzzling including providing & fixing of stay insulator complete in all respect with grouting |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
38 | Fixing of Lead 1x16 Sq mm at Distribution T/F with complete work in all respect. |  | 1 | Mtr | 100 |  |  | Excess(+) | 3356 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
39 | Fixing of LT PVC Cable Al 1x240 Sq mm at Distribution T/F with complete work in all respect. |  | 1 | Meter | 100 |  |  | Excess(+) | 200 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
40 | Fixing of LT XPLE CABLE ALU. 3.5X400SQMM at Distribution T/F with complete work in all respect. |  | 1 | Meter | 100 |  |  | Excess(+) | 40 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
41 | Fixing of Distribution Box with clamp at Pole or site requirement with complete work in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 781 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
42 | Chemical Earthing of T/F : Providing of earth elctrode strip in pipe terminal type chemical earthing proper hot deep galvanization dia 50 mm length 3 mtr down conductor size - 32mm x 6mm terminal connection hole dia 8mm The cavity between the strip & pipes is filled with condutive mixture - for hermetically filling inside the cavity i.e. between secondary conductor & primary conductor, crystline compound is to be injected in the electrode assembly. It is a combination of high conductivity metal alloys, copper & aluminum power, conductive carbon / cement and bonding material etc the electrode should be sealed from both the ends. The outer pipe of the elctrode should be zinc coated the characteristics of this compound is highly cnductive, non magnetic & non corrosive in G.I. Including providing of Pgs backfill compound each elctrode should be supplied with bags of 25 kg x 2 bfc compound (ground resistance enhancement powder 50 kgs each CPRI tested to connect the above chemical earthing with the GI strip of size 32 mm x 6 mm suitable for distribution transformer. |  | 1 | Job | 100 |  |  | Excess(+) | 139 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
43 | Construction of New Plinth for 250KVA & above capacity Distribution Transformers, The size of plinth shall be 2M long 2m wide and the height of the plinth shall be 1.50 M with 20 cm. thick top slab with 02 no. 125x65mm MS channel 2 M long embedded in it. The repairing work includes excavation of earth, laying of brick ballast pad for foundation brickwork, CC and plastering and proper curing. The ratio of cement/course sand/fine sand/brick ballast/stone grit as per RESPO schedule including unloading and Loading of the transformer with complete work in all respect. (All work and material in the scope of the Contractor) |  | 1 | Job | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
44 | Construction of New Fencing of Transformer. The fencing shall be frame of size 1.5mt x1.80 mt fabricated out of MS angle iron of size 40x40x5 mm having 2 Nos. legs of 45 Cm. long in each frameduly welded and fixed with wire mesh of size 75mm 25mm, 10 SWG within the frame, pressed under MS flat of size 25x5 mm inside the angle iron on all four sides with the help of approx. 20 Nos. bolts and nuts. of 10 mm dia along with cross bracing of 25x5 mm MS flat on every frame will be grouted in 1:2:4 cement mortar with cement, coarse sand 20 mm gauge stone ballast in the size 0.22x0.22x0.45 Mtrs. Every frame after repairing will be painted with one coat of red oxide and two coats of blue synthetic enamel paint of approved make after proper cleaning. The above mentioned frame will be jointed with each other with 70 mm long MS flat of size 25x5mm by first class welding as per site. Fabrication and providing of wire mesh fencing frame for gate of size 1.5x180 Mtrs. Fabricated as items no. 2 and fixing of gate frame at each S/S as per site requirement with grouted frame providing 3 Nos. 100 mm size heavy duty hinges duly welded and having suitable locking arrangment and proper painting. |  | 1 | Job | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
45 | Supply and Installation and Commissioning of Horizontal 11KV TPMO for Distribution T/F with complete work in all respect.. |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
46 | Supply of Red Oxide Paint best quality for painting of structure and paint the structure as per site requirement. |  | 1 | Ltr. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
47 | Supply of Alu. Paint best quality for painting of structure and paint the structure as per site requirement. |  | 1 | Ltr. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
48 | Supply and Fixing of Clamps for LT T off with Bolts & Nut as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 100 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
49 | Supply and Fixing of Holding Clamps as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 724 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
50 | Supply and Fixing of Suspention Clamp with 1 Hook as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 842 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
51 | Supply and Fixing of Dead & Clamp with 1 Hook as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 102 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
52 | Supply and Fixing of Peircing Clamp as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 2916 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
53 | Supply and Fixing of All. Lug 400 Sq mm as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
54 | Supply and Fixing of All. Lug 120 Sq mm as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 32 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
55 | Supply and Fixing of All. Lug 35 Sq mm as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 160 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
56 | Supply and Fixing of LT Incomming Pannel with metering as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 49 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
57 | Supply and Fixing of Cooper L-Piece 62x225x12 mm as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 188 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
58 | Supply and Fixing of Cooper L-Piece 50X225X10MMmm as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
59 | Supply and Fixing of Al. Leg Long Barrel off size (LS) as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 744 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
60 | Supply and Fixing of 4 Core LT MCB with Box (LS) as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
61 | Supply and Fixing of Danger Board with clamps as per site requirement. |  | 1 | Nos | 100 |  |  | Excess(+) | 41 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
62 | Dismentaling of old and used 49 Nos. 100KVA T/F and 1 Nos. 160KVA T/F from the different sites under EDD-Dadri, Greater Noida and Jewar and its Safe Carriage to any Store Centre of PVVNL including loading and unloading from both sides. |  | 1 | Job | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information