## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-II, Noida
Name of Work : fctusl Iyku 2025&26 ds vUrxZr fo0u0fo0e0&f}rh;] ukS,Mk ds {ks= esa 33@11 dsoh midsUnzksa dk lqn`<+hdj.k ,oa izksVsD'ku lEcU/kh dk;Z en esa 33dsoh vkj-,e-;w- dh vkiwfrZ o LFkkiuk ls lEcfU/kr 02 ua0 dk;ZA
Contract No: SHORT TERM E-TENDER NO 38/EUDC-II NOIDA/2025-26
G.S.T. INCLUSIVE IN QUOTED RATES.
Name of the Bidder/ Bidding Firm / Company :
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) (Note:- Any type of NOC for the completion of following work will be received by the bidder itself only, Department will not be liable for these NOC.) 2.The rate quoted by the tenderer shall be inclusive of all duties, taxes (INCLUSIVE OF GST), fees, octroi and other levies, materials, any type of NOC, labour to & FOR transportation of material and labour charges etc. ALL TAXES INCLUSIVE IN QUOTED RATES . 3. The work is to be done on SEMI TURNKEY BASIS. 4. All the material and erection practices shall be as per tender specification. 5. Above Schedule Structure and quantities is provisional and may vary as per site requirement with due approval. 6. Indicative scope of works and quantity of Items/Materials required for above work shall be as per the Price Bid. Any other material if required to complete the job and not mentioned above, shall have to be provided by the bidder without additional cost. 7. Financial evaluation and selection of 'L1 Bidder' shall be done on the basis of total amount. The Rates received in the tender will be done final after the approval of competent authority/ committee and competent authority / committee will have the right to negotiate in tender rate. 8. Tenderer must be fill-up the enclosed terms & conditions sheet and attached with 1st Part of Tender as well as scanned copy of same will be uploaded on NIC Website alongwith other documents.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | RATE per unit In Figures To be entered by the Bidder with GST IN Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT with GST in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Providing and Errection of 33KV 6Way RMU at Independent 33KV Society Consumers supply from 220 KV GIS Substation Sector 129, Noida for better supply under EUDD 2 Noida | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Safe Cartage of following centralised stock material from any of the Store Center of PVVNL Discom to work site including Loading from Store and safe unloading at site for Item No. 3 to 4 | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | 33KV HT 3X300SQMM XLPE CABLE |  | 1 | Mtr. | 100 |  |  | Excess(+) | 100 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | 33 KV OUTDOOR JOINTING KIT XLPE 3X300 Sqmm |  | 1 | Nos | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | Errection of above Centralised material and Supply and errection of the below De-Centralised material for completing the works as per RESPO. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | MAKING AND FIXING OF 33KV OUTDOOR TERMINATION KIT SUITABLE FOR 3X300SQMM XLPE CABLE WITH HELP OF JOINTER AND OTHER REQUIRED MATERIAL AND COMPLETE CONNECTIONS IN ALL RESPECT. |  | 1 | Job | 100 |  |  | Excess(+) | 6 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | FIXING AND CONNECTION OF RMU BY 33KV HT 3X300SQMM CABLE AS PER SITE REQUIREMENT WITH COMPLETE WORK IN ALL RESPECT. |  | 1 | Mtr | 100 |  |  | Excess(+) | 100 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | SUPPLY AND INSTALLATION OF RMUs AT PRIMARY SUBSTATION GIS 220KV SECTOR-129 NOIDA FOR UN-INTERUPTTED SUPPLY | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | SUPPLY, INSTALLATION AND PROPER COMMISSIONING OF 33KV, 630 Amps. & extensible, outdoor duty 6-way, fully motorised and manually operated Ring main unit (2 LBS+4 VCB/SF6) consisting of copper busbar in SF6/AIR insulated. RMU should be type tested for internal arc of 25 KA for 1 Sec. for Gas tank, Ingress protection (outdoor) IP54 and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel. Suitable CT with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot for termination Kits Or similar technology. Hermitically sealed stainless steel switching chamber. All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibale easy integration with SCADA networks. (Supply of FRTU is not in scope) Aux. PT, Battery, Charger etc. for Motorised operation by remote control. Circuit Breaker protection using a wide range of self-powered and auxiliary relays. Accessible cable Earth & Test Facility at the front of the unit. The scope is including Plinth and Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories. ( Makes: ABB / Siemens / Eaton / Schneider/Lucy/any other make approved in UPPCL) FOR 33KV BAY with complete work in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | Construction of Plinth of size 6'x3'x3' (LxWxH) for above RMUs complete in all respect. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | PROVIDING AND INSTALLATION OF CHEMICAL EARTHING FOR ABOVE RMUs (WITH ALL MATERIAL AND LABOUR) AFTER INSTALLATION RESISTANCE SHOULD BE LESS THAN ONE OHM. AS PER FOLLOWING (The all material and labour shall be provided by the contractor with 12 month guarantee for resistance value less than one OHM.) | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | Chemical Earthing of Installed RMU as per site requirement as per specification. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | Providing and fixing of GI strip of size 32 mm x 6 mm suitable for RMUs installed at Above 33/11 KV Substation . |  | 1 | Mtr | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. |  | 1 | Mtr | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | Providing and Errection of 33KV 6Way RMU in 33KV Bay No. 12 supply from 220 KV GIS Substation Sector 129, Noida for better supply under EUDD 3 Noida | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | Safe Cartage of following centralised stock material from any of the Store Center of PVVNL Discom to work site including Loading from Store and safe unloading at site for Item No.17 | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | 33KV HT 3X300SQMM XLPE CABLE |  | 1 | Mtr. | 100 |  |  | Excess(+) | 100 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Errection of above Centralised material and Supply and errection of the below De-Centralised material for completing the works as per RESPO. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | FIXING AND CONNECTION OF RMU BY 33KV HT 3X300SQMM CABLE AS PER SITE REQUIREMENT WITH COMPLETE WORK IN ALL RESPECT. |  | 1 | Mtr | 100 |  |  | Excess(+) | 100 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | SUPPLY AND INSTALLATION OF RMUs AT PRIMARY SUBSTATION GIS 220KV SECTOR-129 NOIDA FOR UN-INTERUPTTED SUPPLY | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
21 | SUPPLY, INSTALLATION AND PROPER COMMISSIONING OF 33KV, 630 Amps. & extensible, outdoor duty 6-way, fully motorised and manually operated Ring main unit (2 LBS+4 VCB/SF6) consisting of copper busbar in SF6/AIR insulated. RMU should be type tested for internal arc of 25 KA for 1 Sec. for Gas tank, Ingress protection (outdoor) IP54 and cable chamber with AFLR classification and gas to be from rear bottom of the switchgear away from the operator to ensure safety of the operating personnel. Suitable CT with microprocessor based numerical over current relay (IDMTL + Inst.) for Protection to be provided with VCB Feeder with right angle boot for termination Kits Or similar technology. Hermitically sealed stainless steel switching chamber. All the necessary wirings and Dummy panel /space for FRTU to be given along with RMU for future compatibale easy integration with SCADA networks. (Supply of FRTU is not in scope) Aux. PT, Battery, Charger etc. for Motorised operation by remote control. Circuit Breaker protection using a wide range of self-powered and auxiliary relays. Accessible cable Earth & Test Facility at the front of the unit. The scope is including Plinth and Angle iron Stand as per OEM design complete in all rescept as per the direction of Engineer incharge. Complete RMU and its accessories. ( Makes: ABB / Siemens / Eaton / Schneider/Lucy/any other make approved in UPPCL) FOR 33KV BAY with complete work in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | Construction of Plinth of size 6'x3'x3' (LxWxH) for above RMUs complete in all respect. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
23 | PROVIDING AND INSTALLATION OF CHEMICAL EARTHING FOR ABOVE RMUs (WITH ALL MATERIAL AND LABOUR) AFTER INSTALLATION RESISTANCE SHOULD BE LESS THAN ONE OHM. AS PER FOLLOWING (The all material and labour shall be provided by the contractor with 12 month guarantee for resistance value less than one OHM.) | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
24 | Chemical Earthing of Installed RMU as per site requirement as per specification. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25 | Providing and fixing of GI strip of size 32 mm x 6 mm suitable for RMUs installed at Above 33/11 KV Substation . |  | 1 | Mtr | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
26 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. |  | 1 | Mtr | 100 |  |  | Excess(+) | 4 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | Replacement of Jarjar 33 KV 3x400 Sqmm XLPE Cable and 33 KV 3x300 Sqmm XLPE Cable for Eco City, Imperial Housing & Purvanchal Society, Sector-137, Noida Under EUDD-III, Noida | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
28 | Safe Cartage of following centralised stock material from any of the Store Center of PVVNL Discom to work site including Loading from Store and safe unloading at site for Item No.29 to 32. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
29 | 33 KV 3x400 Sqmm XLPE Cable |  | 1 | Mtr. | 100 |  |  | Excess(+) | 1800 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
30 | 33 KV 3x300 Sqmm XLPE Cable |  | 1 | Mtr. | 100 |  |  | Excess(+) | 300 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
31 | 33 KV Outdoor Jointing Kit for 3x400 Sqmm Cable |  | 1 | Nos. | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
32 | 33 KV Outdoor Jointing Kit for 3x300 Sqmm Cable |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
33 | Errection of above Centralised material and Supply and errection of the below De-Centralised material for completing the works as per RESPO. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
34 | Supply of 140mm OD PN-6-PE-80, 6" Dia Grade UV Stabilized HDPE Pipe.(PVVNL GTP APPROVED) |  | 1 | Mtr | 100 |  |  | Excess(+) | 1900 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
35 | Drilling of dia 220 mm in bores for Double Curcuit by trenchless method by horizontal boring machine at a depth of 1.50 mtrs to 2.50 mtrs. (as per site requirement) below the ground level for 3x300Sqmm and 3x400sqmm XLPE Cable at Kaccha/Pakka Road/Road Crossing/as per site requirement with complete work in all respect as per RESPO. Road Restoration charges shall be inclusive in quoted rates. |  | 1 | Mtr | 100 |  |  | Excess(+) | 1900 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
36 | Laying and interconnecting of above HDPE Pipe PE-80, PN6, DN-140mm, 6" dia by HDD trenchless method for HOSTING OF 33 KV 3x300sqmm and 3x400sq.mm XLPE cable in Double Circuit with complete work in all respect. |  | 1 | Mtr | 100 |  |  | Excess(+) | 1900 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
37 | Laying, Hosting and commissiong of 33 KV 3x300sqmm and 3x400sq.mm XLPE Cable Double Ckt. Cable in HDPE Pipe in HDD trenchless method with complete work in all respect. |  | 1 | Mtr | 100 |  |  | Excess(+) | 1900 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
38 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop and making risers at double pole and re-filling of pits in proper manner with required material at kacha/pakka and hot mix road. (All Work and material in the scope of contractor) Road Restoration charges shall be inclusive in quoted rates. |  | 1 | Job | 100 |  |  | Excess(+) | 5 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
39 | Preparation, Making and Fixing of 33 KV Power Cable ends: Fixing and Making of 33 KV 3x300sqmm and 3x400sq.mm XLPE Heat shrinkable outdoor jointing kits suitable for 33 KV 3x300sqmm and 3x400sq.mm XLPE after duly plumbing and taping of cable, providing, fixing and crimping of proper size good quality lugs with complete connention in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 5 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
40 | Laying and Loopping of 33 KV 3x300sqmm and 3x400sq.mm XLPE Cable Double Ckt. in the air on cable Riser Double Pole existing trench cable trench with G.I.Pipe and making connection complete at both ends. Road Restoration charges shall be inclusive in quoted rates. |  | 1 | Mtr | 100 |  |  | Excess(+) | 200 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
41 | Dismentaling of old and Damaged 33 KV 3x300sqmm and 3x400sq.mm XLPE underground cable from the different sites at kacha/pakka road and Safe carriage of its from site to any PVVNL Store including loading and unloading both ends. Pakka Road Resotration Charges in the scope of contractor. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #REF! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information