## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, EUDC-I, Noida
Name of Work: DETAILS OF WORK AND QUANTITY AGAINST E-TENDER NO. 29/EUDC-I/2025-26/NOIDA (WORKS) FOR CARRYING OUT THE 01 NO. WORK IN HEAD REPLACEMENT OF 33 KV VCB AS PER DPR S.NO. 1 & PROTECTION & STRENGTHENING OF 33/11 KV SUBSTATIONS AS PER DPR S.NO. 5, 6, 7, 8, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 22 UNDER EUDD-V & EUTD-I, NOIDA IN THE JURIDICTION OF EUDC-I, NOIDA (BUSINESS PLAN F.Y. 2025-26).
Contact No: 0120-2970431
The bidder quoted rate should be inclusive GST & all other taxes.
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only ) Note:- 1. The bidder quoted rate should be inclusive GST & all other taxes. 2. In case the tenderer quotes impractical rates for the work and does not enter into a contract, action will be taken to confiscate the earnest money of the tenderer and blacklist the firm. 3. In case the tenderer quotes rates for material such as Relay / Cable / Feeder Panel / Earthing / Pipe which are impractical as compared to the current market rate, then the contractor shall have to deposit 10% of the total contract amount as Performance Bank Guarantee for a period of 02 years. 4. Payment will be done after complete execution of work/ entire project & submission of executed estimate and after getting satisfactory report in all respect from concern SDO/JE.
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Unit | Estimated Rate in Rs. P |  |  | Addition / Deduction | Quantity | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder with GST & all other taxes Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 3 | 6 | 7 | 8 | 9 | 4 | 11 | 5 | 6 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Cartage of following material from ESC Noida/Sahibabad/ Ghaziabad /Any other ESC of Meerut Discom to JE Store and from JE store to various points site of work including loading and unloading at both ends : - | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.01 | 11 KV XLPE Cable 3x300 Sq.mm. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | 11 KV XLPE Cable 3x185 Sq.mm. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 2000 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.03 | 11 KV Cable Jointing Kit I/D 3x300 Sq.mm. |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.04 | 11 KV Cable Jointing Kit O/D 3x300 Sq.mm. |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.05 | 11 KV Cable Jointing Kit O/D 3x185 Sq.mm. |  | 1 | Nos. | 100 |  |  | Excess(+) | 234 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.06 | 11 KV Polymeric Disc Insulator with fitting |  | 1 | Nos. | 100 |  |  | Excess(+) | 234 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.07 | T-Off channel |  | 1 | Nos. | 100 |  |  | Excess(+) | 78 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.08 | 11 KV Stay Set |  | 1 | Nos. | 100 |  |  | Excess(+) | 78 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.09 | 33 KV Isolator / TPMO Set |  | 1 | Nos. | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.1 | 33 KV Fuse Set with Structure |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.11 | 33 KV Breaker |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.12 | 33 KV Control Pannel, I/C for 33 KV Double T/F |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.13 | 33 KV Control Pannel, I/C for 33 KV Single T/F |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.14 | 33 KV Fuse Set 800A |  | 1 | Nos. | 100 |  |  | Excess(+) | 7 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.15 | 33 KV Line Isolator 800A |  | 1 | Nos. | 100 |  |  | Excess(+) | 5 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.16 | 33 KV Bus Isolator 800A |  | 1 | Nos. | 100 |  |  | Excess(+) | 7 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Erection, installation and fixing of following material as per RESPO norms complete in all respect : - | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.01 | Laying of 11 KV XLPE Cable 3x300 Sq.mm. from power transformer to incoming panel at 33/KV Substation. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.02 | Laying of 11 KV XLPE Cable 3x185 Sq.mm. for interconnection of feeders/branches with RMU at various location. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 1480 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.03 | 11 KV Cable Jointing Kit I/D 3x300 Sq.mm. |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.04 | 11 KV Cable Jointing Kit O/D 3x300 Sq.mm. |  | 1 | Nos. | 100 |  |  | Excess(+) | 10 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.05 | 11 KV Cable Jointing Kit O/D 3x185 Sq.mm. |  | 1 | Nos. | 100 |  |  | Excess(+) | 234 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.06 | 11 KV Polymeric Disc Insulator with fitting |  | 1 | Nos. | 100 |  |  | Excess(+) | 234 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.07 | T-Off channel |  | 1 | Nos. | 100 |  |  | Excess(+) | 78 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.08 | 33 KV Isolator / TPMO Set |  | 1 | Nos. | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.09 | 33 KV Fuse Set with Structure |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.1 | 33 KV Fuse Set 800A |  | 1 | Nos. | 100 |  |  | Excess(+) | 7 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.11 | 33 KV Breaker |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.12 | 33 KV Control Pannel, I/C for 33 KV Double T/F |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.13 | 33 KV Control Pannel, I/C for 33 KV Single T/F |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.14 | 33 KV Line Isolator 800A |  | 1 | Nos. | 100 |  |  | Excess(+) | 5 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2.15 | 33 KV Bus Isolator 800A |  | 1 | Nos. | 100 |  |  | Excess(+) | 7 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | Grouting & concreting of stay rod 1800x16 mm & Fixing, Tighting & nozzling of stay wire 5 kg with the pole of required tension with clamps, bolt & nut. |  | 1 | Nos. | 100 |  |  | Excess(+) | 78 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | Providing & fixing of following material of standard make / best quality for complete the work of system strengthening of 33/11 KV Substation as per RESPO norms by the contractor at his own cost : - | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.01 | 33 KV Fuse Set Structure |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.02 | Clamp with Nuts & Bolts |  | 1 | Nos. | 100 |  |  | Excess(+) | 78 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.03 | G.I. Pipe 6" Dia. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 234 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.04 | LT Lead suitable for Feeder Panel connection. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 60 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4.05 | Sundries Item for replacement of 33 KV Fuse Set with Structure. |  | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5 | Dismantling of following item from various site of work and carriage from work site to J.E's store / central store including loading & unloading at both ends. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5.01 | Old & Damaged 33 KV Isolator / TPMO Set |  | 1 | Nos. | 100 |  |  | Excess(+) | 8 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5.02 | 33 KV Line / Bus Isolator (Scrap) |  | 1 | Nos. | 100 |  |  | Excess(+) | 12 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5.03 | 33 KV Breaker |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5.04 | 33 KV Control Pannel, I/C for 33 KV Double T/F |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5.05 | 33 KV Control Pannel, I/C for 33 KV Single T/F |  | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5.06 | Old & damaged LT Feeder Panel Box |  | 1 | Nos. | 100 |  |  | Excess(+) | 3 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6 | REPLACEMENT OF OLD & DAMAGED LT FEEDER PILLER (MAIN / BRANCH PANNEL) OF VARIOUS SECTORS IN AREA OF EUDSD-VIII / IX, NOIDA AS PER FOLLOWING :- | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6.01 | Supply of new L.T. Feeder Pillar (Main Pannel) as per following specification with all relevant certificate :- 1) LT Feeder Pillar Box (Main Pannel) shall be of 14 SWG HR sheet, having (1) doors in front of 14 SWG HR sheet. Doors should have proper locking arrangements with providing crome locks of standard make. It should have a canopy on top in order to prevent it from water ingress in rains. The doors of box should be welded with robust quality hinges and PVC GaskEt with provision of 3 hinges on each door and handle on each door with PVC Gasket. The periphery of door of the LT Feeder Pillar Box (Main Pannel) shall be provided with lining of rubber/ PVC to prevent entry of rain, insects, lizards, rats etc. so as to make it vermin proof. 2) The dimension of Feeder Pillar Box (Main Pannel) 4(Height) X 2.5(Width) X 2(Depth) Feet (With Canopy). 3) 04 Nos. Bus Bar insulation coated fo size 600x75x10mm. made of aluminum for red, yellow, blue & neutral phases suitable for 600 Amp. 4) 01 No. MCCB of 600 Amp. of L&T / Havell’s / ABB / PVVNL APPROVED make for disconnecting of Supply. 5) 24 Nos. HRC Fuse of 415V, 200 Amp. each capacity tested as per IS shall be provided with 8 Nos. on each phase so as to cater to 8 Nos. 3 Phase connections of conusmer. 6) Aluminum crimping lugs of size 400 / 240 / 120 / 95 / 70Sq.mm. and proper size thimbles shall be provided for safe termination of incomer as well as individual service cable as per qty. requirement. 7) Bakelite sheet shall be provided on the base of channel meant for mounting the Kit Kats. 8) All nuts, bolts & washers used shall be electro galvanized. 9) The height of erected feeder pillar box (Main Pannel) approx. 2 feet from the earth on powder coating base of angle iron size 40x40x5mm frame with 04 nos. legs of 3 feet each (1 feet grout of angle on earth bottam, 1.6 feet grout in plinth and 6 inch gap in pannel base and plinth) 10) Grouting & Plinth of Feeder Pillar Box (Main Pannel) as per site requirement complete in all respects. 11) The panel case consisting of door and roof (canopy) shall be powder coated with chemical process (weather proof) of Off-white color (Or as per direction) both inside and outside. Before painting, the sun faces shall be thoroughly cleaned from dust, grease and rust. Ientification no. shall be written as per direction. 12) Sundry item. |  | 1 | Nos. | 100 |  |  | Excess(+) | 27 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6.02 | Supply of new L.T. Feeder Pillar (Branch Distribution Pannel) as per following specification with all relevant certificate :- 1) LT Feeder Pillar Box (Branch Distribution Pannel) shall be of 14 SWG HR sheet, having (1) doors in front of 14 SWG HR sheet. Doors should have proper locking arrangements with providing crome locks of standard make. It should have a canopy on top in order to prevent it from water ingress in rains. The doors of box should be welded with robust quality hinges and PVC GaskEt with provision of 3 hinges on each door and handle on each door with PVC Gasket. The periphery of door of the LT Feeder Pillar Box (Branch Distribution Pannel) shall be provided with lining of rubber/ PVC to prevent entry of rain, insects, lizards, rats etc. so as to make it vermin proof. 2) The dimension of Feeder Pillar Box (Branch Distribution Pannel) 4(Height) X 2.5(Width) X 2(Depth) Feet (With Canopy). 3) 04 Nos. Bus Bar insulation coated fo size 600x75x10mm. made of aluminum for red, yellow, blue & neutral phases suitable for 400 Amp. 4) 01 No. MCCB of 400 Amp. of L&T / Havell’s / ABB / PVVNL APPROVED make for disconnecting of Supply. 5) 18 Nos. KIT KAT Fuse of 415V, 150 Amp. each capacity tested as per IS shall be provided with 6 Nos. on each phase so as to cater to 6 Nos. 3 Phase connections of conusmer. 6) Aluminum crimping lugs of size 400 / 240 / 120 / 95 / 70Sq.mm. and proper size thimbles shall be provided for safe termination of incomer as well as individual service cable as per qty. requirement. 7) Bakelite sheet shall be provided on the base of channel meant for mounting the Kit Kats. 8) All nuts, bolts & washers used shall be electro galvanized. 9) The height of erected feeder pillar box (Branch Distribution Pannel) approx. 2 feet from the earth on powder coating base of angle iron size 40x40x5mm frame with 04 nos. legs of 3 feet each (1 feet grout of angle on earth bottam, 1.6 feet grout in plinth and 6 inch gap in pannel base and plinth) 10) Grouting & Plinth of Feeder Pillar Box (Branch Distribution Pannel) as per site requirement complete in all respects. 11) The panel case consisting of door and roof (canopy) shall be powder coated with chemical process (weather proof) of Off-white color (Or as per direction) both inside and outside. Before painting, the sun faces shall be thoroughly cleaned from dust, grease and rust. Ientification no. shall be written as per direction. 12) Sundry item. |  | 1 | Nos. | 100 |  |  | Excess(+) | 50 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6.03 | Disconncetion of all Consumer connection from pannel as per requirement. |  | 1 | Jobs | 100 |  |  | Excess(+) | 77 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6.04 | Reconncetion of all Consumer connection from pannel after replacement as per requirement. |  | 1 | Jobs | 100 |  |  | Excess(+) | 77 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
6.05 | Installation of above new L.T. Feeder Pillar (Main / Branch Distribution Pannel) in place of damaged L.T. Feeder Pillar (Branch Distribution Pannel) with grouting, plinth and required items complete in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 77 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | Supply and Installation of Different Types of Relay (Master, Over Current Earth Short Relay, WTI, OTI) at various 33/11 substations in the jurisdiction of EUDC-I, Noida. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.01 | Supply of IDMT Protection Relay with Numerical Micro controller based 4 Pole, 3 O/C + 1 E/F suitable for various type of 11 KV control panel reply replacement of Type ADR 141A. Features : Auxiliary voltage : 18-230 V A.C./D.C CT secondary 1/5 Amp. and 1 Amp. suitable for various make 11 KV Breaker and control Panels. |  | 1 | Nos. | 100 |  |  | Excess(+) | 52 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.02 | Supply of IDMT Protection Relay with Numerical Micro controller based 4 Pole, 3 O/C + 1 E/F suitable for various type of 33 KV control panel reply replacement of Type ADR 141A. Features : Auxiliary voltage : 18-230 V A.C./D.C CT secondary 1/5 Amp. and 1 Amp. suitable for various make 33 KV Breaker and control Panels. |  | 1 | Nos. | 100 |  |  | Excess(+) | 36 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.03 | Supply of Master Relay with Model : CLR, Operating Voltage : 24 VDC, No. of NO Contact : 3 NO Contact, No. of NC Contact : 2 NC Contact, suitable for various make Breaker. |  | 1 | Nos. | 100 |  |  | Excess(+) | 22 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.04 | Supply of Winding Temperature Indicator 6" Dia having range 0-120C with MRP Pointer (Double contact for alamr and trip) with 3 meter long PVC capillary and Brass Contact 9" long suitable for 33/11KV Substations 3/5/10 MVA Transformers. |  | 1 | Nos. | 100 |  |  | Excess(+) | 32 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.05 | Supply of Oil Temperature Indicator 6" Dia having range 0-120C with MRP Pointer (Double contact for alarm and trip) with 3 meter long PVC capillary and Brass Contact 9" long suitable for 33/11KV Substations 3/5/10 MVA Transformers. |  | 1 | Nos. | 100 |  |  | Excess(+) | 32 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.06 | Supply of Control cable 4x2.5 Sq.mm. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 700 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8 | Installation of Different Types of Relay (Master, Over Current Earth Short Relay, WTI, OTI) & cable at various 33/11 substations in the jurisdiction of EUDC-I, Noida. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8.01 | INSTALLATION OF ABOVE RELAY AT DIFFERENT SUBSTATIONS AS PER SITE REQUIREMENT WITH COMPLETE WORK AND CONNECTION IN ALL RESPECT. |  | 1 | Job | 100 |  |  | Excess(+) | 110 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8.02 | LAYING OF CONTROL CABLE AT DIFFERENT SUBSTATIONS AS PER SITE REQUIREMENT WITH COMPLETE WORK AND CONNECTION IN ALL RESPECT. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 700 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9 | UNSTALLING, REPAIRING AND REINSTALLING THE DAMAGED 30 NOS. 11 KV PTs TO STREAMLINE THE METERING SYSTEM AND TO REPAIR THE DAMAGED WIRING INSTALLED AT VARIOUS 33/11 KV POWER SUB-STATIONS IN AREA OF EUTL-I/V/VII, NOIDA UNDER EUTD-I, NOIDA AS PER FOLLOWING :- Note :- The material of PTs repairing shall be provided by the contractor. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9.01 | Repairing of damaged 11 KV PTs to streamline the metering system and to repair the damaged wiring with opening, uninstalling and reinstalling of PTs / Wiring complete in all respect. |  | 1 | Nos. | 100 |  |  | Excess(+) | 30 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | CHEMICAL EARTHING WORK (SUPPLY AND INSTALLATION) OF FEEDER PILLAR BOX / SUBSTATION SWITCHGEAR AS PER FOLLOWING:- Note :- The all material and labour shall be provided by the contractor with 24 month guarantee for resistance value less than one OHM. | [53 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10.01 | Providing of earthing electrode :- Material Description : GI Electrode, Galvanization : 150 Micron (Min), IS Standard : IS 3043 / IEEE - 837, Short Time Current Rating kA (rms) For 1 Sec : 42 KA For 1 Sec, Dia of Electrode : 50mm, Length of Electrode : 3000mm, Weight of Electrode : 15 Kgm, Pipe Thickness : 4mm or As per IS : 1239 4mm, Inside Filling Material : Crystalline Conductive Mixture, Inner Strip : 3100 X 50 X 6 mm, Terminal Hole Dia : 16 MM. Technology : Metal Thermal Spray (Joints) Protection Earthing Resistance Value in Different Soil Conditions with ERIC Backfill Compound : Normal Soil - Upto 2 Ohms, Sand. Muran Soil - Upto 4 Ohms, Rock Soil - Upto 4 Ohms, Electrode Testing Cetificate : CPRI Testd. Surrounding Filling Material (ERIC):- Product : ERIC (Earth Resitance Improvement Compound), IS Standard : IS 3043/IEEE 837, Chemical Composition : Graphite, Activated Carbon, Bentonite, ETC., Resistivity Value : >0.2 Ohm Per Meter, Melting Temperature : 2500 Degree Centigrade, Specific Gravity : 2.6, PH Value of Chemical : 7-9, Solubility in water : 3.54, Colour : Light cream/Ash, Main Caution ; Sodium, Moisture Capacity at 105 Degree : 10%, Weight of Chemical used / Earthing Pit : 50 Kg, Water Absorbing Capacity : 20 Times, Environmental Effects : Eco Friendly. Test Certifictae : ROHS Certified, Thermal Stability : Testsed, Corrosion Resistance : Tested, Swell Test Certificate : Yes, Ph Value Test Certificate : Yes. Installation Parameter :- Need Hole Dia : 6"-8" Need Hole Depth : 3 Meter, Guarantee : 24 Month. |  | 1 | Nos. | 100 |  |  | Excess(+) | 94 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10.02 | Providing and fixing of GI strip of size 50 mm x 6 mm suitable for Feeder Pillar Box / Substation Switchgear installed at various site. |  | 1 | Nos. | 100 |  |  | Excess(+) | 282 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10.03 | Providing and fixing of PVC Pit covers for above earthing electrode terminals. |  | 1 | Nos. | 100 |  |  | Excess(+) | 94 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | Drilling of suitable dia 140 mm by trenchless method by horizontal boring machine at a depth of 1.5 mtrs below the ground level for replacement / laying of 11 KV XLPE 3x185 Sq.mm. cable with Road Restoration in accordance with GPR Survey. Any damage to Road part from estimate shall be responsibility of contractor shall take NOC permission from concerned Authority & Restore as per their norms. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 520 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12 | Providing of 06 Mtr long pieces of HDPE pipe PN 4, PE 63, 140mm Dia (PVVNL approved) after inspection of competent committee at manufacturing site of the items with actual guarantee period. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 520 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
13 | Laying and interconnecting of above 06 Mtr long pieces of HDPE pipe PN 4, PE 63, 140mm Dia (PVVNL approved) in trench for laying of 11 KV XLPE 3x185 Sq.mm. cable complete in all respects.. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 520 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | Digging of pits of size 4 mtr x 4 mtr x 1.5 mtr for cable loop. |  | 1 | Nos. | 100 |  |  | Excess(+) | 2 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15 | Providing of HDPE Socket suitable for HDPE pipe 140mm dia HDPE Pipe . |  | 1 | Nos. | 100 |  |  | Excess(+) | 90 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16 | Fixing of above HDPE Socket suitable for HDPE pipe 140mm dia HDPE Pipe . |  | 1 | Nos. | 100 |  |  | Excess(+) | 90 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | Geo-tagging of complete work as per PVVNL order No. 1919 Dated 23.08.2025 (Letter attached with condition). |  | 1 | Job. | 100 |  |  | Excess(+) | 16 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18 | Tree prunning / cutting as per work site requirement. |  | 1 | Job | 100 |  |  | Excess(+) | 5 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | Laying and pulling of 11 XLPE Cable 3x185 Sq.mm. Cable through HDPE pipe complete in all respects. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 8400 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | Hi port test for 11 KV XLPE Cable 3x185/300 Sq.mm. |  | 1 | Mtrs. | 100 |  |  | Excess(+) | 2500 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!

## Macros
Please Enable Macros to View BoQ information